## Field Demonstration Checklist
# | Quantity | Units | Reported value | Recommendation
1 | Test duration | Days |  | Test advanced control for at least seven days, and ideally for one month or longer.
2 | Benchmarking method | - |  | Compare advanced control performance to the measured performance of a baseline controller in the same building or a nearby, similar building.
3 | Controlled portion of building | - |  | Control a whole building, control a large subset of a building that is well-insulated from adjacent zones, or account in savings calculations for heat transfer between controlled zones and adjacent zones.
4 | Controlled floor area | m² or ft² |  | Report the floor area of the controlled zone or building to contextualize the scale of the demonstration.
5 | Costs, labor, and other challenges | Time (e.g., hours) and/or cost (e.g., USD) |  | Distinguish between one-time costs (such as training junior researchers to implement advanced control, or selecting appropriate instrumentation and algorithms) vs. recurring costs (such as instrumenting a building, establishing data access and communication, on-boarding a building into a pre-existing software system, commissioning systems, and tuning controllers) that a company would need to repeat for each new building.
6 | Type of test building | - |  | Prefer field sites over laboratories to ensure realistic test conditions, for both residential and commercial buildings. Use laboratories when greater reproducibility is needed.
7 | Electricity rate structure | - |  | Specify whether the electricity rate structure includes a time-invariant price, time-of-use prices with two or more price tiers, hourly prices, critical peak prices, peak demand charges, or incentives for distribution-level demand response or transmission-level ancillary services.
8 | Space conditioning mode(s) | - |  | Clearly report whether the controller was tested in heating, cooling, or both modes. When testing both, separate the reported results by mode to avoid aggregating distinct effects.
9 | HVAC equipment type | - |  | For example, central chiller plant, rooftop unit, residential split-system, etc.
10 | Date of building construction or latest renovation | - |  | -
11 | Thermal mass of building | - |  | Describe the building’s thermal mass using measured capacitance if available. Otherwise provide a qualitative description (e.g., thermally light vs. heavy), based on construction materials and structure type.
12 | Insulation level of building | - |  | Report the building’s insulation level through metrics like thermal resistance (R-value). If unavailable, provide a qualitative assessment (e.g., well-insulated vs. poorly insulated, drafty vs. tight).
13 | Control architecture | - |  | Specify whether the controller adjusted high-level setpoints (e.g., zone air temperatures) or low-level actuator positions (e.g., equipment on/off state, valve position, fan speed, compressor speed).
14 | Algorithm implementation choices | - |  | Report key implementation details such as model type, forecasting method, optimization or training approach, solver used (for MPC), and exploration strategy (for RL). Clearly describe how system dynamics, constraints, and control objectives were handled.
15 | Climate zone | - |  | Report the climate zone of the test site (e.g., hot, cold, mixed; dry, humid, marine).
16 | Coordination with other DERs | - |  | Indicate whether the study coordinates HVAC control with other DERs (e.g., EVs, batteries, thermal storage, PV).