## residential (papers)
| Paper | Year | # of tests | Control method | Publication venue | Field site or laboratory? | Location | Country | Continent | Building description | HVAC system | Controlled space | Whole building or subset of building? | Floor space (m2) | Test duration (days) | Climate zone | Heating, cooling, or both | Control action (high level vs low level) | Solver details (MPC) | System model (MPC) | Forecasting (MPC) | Optimization problem (MPC) | RL setup (RL) | Action space (RL) | State space (RL) | Learning objective (RL) | Benchmark | Confidence interval? | Electricity savings (%) | Thermal energy savings (%) | Cost savings (%)
1 | Pedersen et al. (2013) | 2013 | 1 | MPC | 2013 10th IEEE INTERNATIONAL CONFERENCE ON NETWORKING, SENSING AND CONTROL (ICNSC) | Field site | Denmark | Denmark | Europe | four single-family detached houses | radiant floor heating with ground-to-water heat pumps (HPs) | Whole building | Whole building |  | 152 | 5A | Heating | High |  | Continuous-time grey-box thermal model with RC analogy Linear - 5 minutes (model identification), 60 minutes (optimization) - | Weather (ambient temperature, solar radiation), Electricity price External forecast input (e.g., weather service), N/A for price 36 hours | Cost Mixed hard-soft (comfort bounds as soft constraints, energy and power limits as hard constraints) Heat pump energy consumption per hour |  |  |  |  | Measurement | No |  |  | 9.17
2 | Dong and Lam (2014) | 2014 | 2 | MPC | Building Simulation | Laboratory | Pittsburgh , USA | United States | North America | a sustainable house, visitor location | radiant floor heating and forced-air cooling with fixed settings | Whole building | Whole building | 67.5 | 10 | 4A | Heating Cooling | High | Nonlinear Custom (Dynamic Programming) Not guaranteed | 3R2C RC network model Nonlinear - 60 (heating), 15 (cooling) Manufacturer data (water heater) | Weather (temperature, solar radiation, wind), Occupancy Hammerstein-Wiener model (weather), Adaptive Gaussian Process, Hidden Markov Model, Semi-Markov Model (occupancy) 3 hours (cooling), 24 hours (heating) | Energy - Water temperature rise, Water flow rate, Supply air flow rate |  |  |  |  | Simulation | No
3 | Lindelöf et al. (2015) | 2015 | 10 | MPC | Energy and Buildings | Field site | Brugg, Fey, Hedingen, Ihmert, Lausanne, Ludenscheid, Remscheid, Ruswil, Sprockhoevel, Unterengstringen | Switzerland and Germany | Europe | eight single-family houses and two apartments | radiant with water distribution; sources include wood pellets, HPs, gas, and oil | Whole building | Whole building | 180 Brugg, 240 Fey, 130 Hedingen, 110 Ihmert, 280 Lausanne, 65 Ludenscheid, 260 Remscheid, 200 Ruswil, 220 Sprockhoevel, 200 Unterengstringen | 61 Brugg, 113 Fey, 81 Hedingen, 27 Ihmert, 64 Lausanne, 94 Ludenscheid, 65 Remscheid, 138 Ruswil, 36 Sprockhoevel, 95 Unterengstringen | 5A | Heating | High | Constrained nonlinear optimization - - | Adaptive model using system identification with a self-learning algorithm - - 15 minutes (900 seconds) - | Outdoor temperature, solar irradiance Self-learning model updated from sensor data 24 hours | Energy and comfort (minimize flow temperature while maintaining thermal comfort) Quadratic penalty on the deviation from the indoor temperature setpoint with a minimum temperature constraint (soft comfort during occupied periods, hard lower bound at all times) Flow temperature |  |  |  |  | Measurement | Yes
4 | Leurs et al. (2016) | 2016 | 1 | RL | 2016 IEEE International Energy Conference (ENERGYCON) | Laboratory | Leuven, Belgium | Belgium | Europe | living lab setup featuring a test room | forced-air integrated with PV system | Test room | Subset of building | 61.62 | 3 | 4A | Cooling | High |  |  |  |  | Q-learning RC (resistance-capacitance) model | HVAC on/off two | time, indoor temperature, outdoor temperature, and PV power four | minimizing the net power squared (i.e., the squared difference between HVAC power consumption and PV power generation) Boltzmann exploration | Measurement | No
5 | Zong et al. (2017) | 2017 | 1 | MPC | Applied Thermal Engineering | Field Site | Roskilde, Denmark | Denmark | Europe | single family detached house | radiant water-based heating with electro-valve radiators | Whole building | Whole building | 150 | 10 | 5A | Heating | Low | Linear Programming (LP) - - | RC network Linear Six-state model (TiTe) with three indoor and three envelope temperatures 60 minutes - | Weather (ambient temperature, solar irradiation), Electricity price - 48 hours (forecast data), 5 hours (EMPC horizon in results) | Minimize electricity cost based on dynamic day-ahead price signals Mixed hard-soft (comfort temperature constraints handled with soft constraints) Radiator heating power (manipulated via electro-valves) |  |  |  |  | Simulation | No | 5% for PID Average and -3.2% for PID low |  | 11.3
6 | Afram and Janabi-Sharifi (2017) | 2017 | 1 | MPC | Energy and Buildings | Laboratory | Vaughan, Ontario, Canada | Canada | North America | four-story sustainable house, including a basement, with an adjacent in-law suite | hybrid system with radiant heating, forced-air cooling, and a ground source HP with a buffer tank | Whole building | Whole building | main home has floor area of 317 m2 (3412 ft 2). In-law suite has 6.7 m × 3.81 m and same envelope as main home. (25.53 m2) | Cooling test: 22 Heating test: - | 5A | Cooling | High | Not explicitly stated; likely LP or QP (Quadratic Programming) due to linear models and cost-based objective APMonitor (solver unspecified) - | Grey-box heat balance equations (physics-based with fitted parameters) Linear - - Physics-inspired equations using measured parameters; approximated as linear models (e.g., heat balance, thermal conductance) | Weather, Electricity price Weather data from Meteorological Service of Canada; electricity price from published TOU schedule (Schedule-based) 24-48 hours | Cost and energy minimization based on electricity time-of-use (TOU) pricing and power consumption of HVAC subsystems Hard only -- applied to zone temperatures, buffer tank water temperatures, and control signals (0-1 bounds) Zone temperature set-points, buffer tank set-points |  |  |  |  | Simulation | No |  |  | 16-142.3
7 | Bünning et al. (2020) | 2020 | 1 | MPC | Energy and Buildings | Field site | Dübendorf, Switzerland | Switzerland | Europe | residential module in a sustainable demonstrator building | air-to-water HP with hydronic radiant ceilings and room-specific valves | Apartment bedroom | Subset of building | 17.6 | 6 | 5A | Cooling | Low | QP - - | Random forest with affine functions Linear in control inputs - 60 minutes - | Ambient temperature, solar radiation External weather forecasts (MeteoSwiss), autoregressive terms 6 hours | Minimize cooling energy Soft upper and lower bounds on indoor temperature (thermal comfort) Valve actuation levels over the prediction horizon |  |  |  |  | Measurement | No
8 | Finck et al. (2020) | 2020 | 2 | MPC | Applied Energy | Field site | near Amstelveen, Netherlands | Netherlands | Europe | detached four-story low-energy house | hydronic floor heating supplied by an HP powered by PV thermal panels | Whole building | Whole building | 345 | 1 and 1 | 4A | Heating | High |  | ANN, Grey-box (multi-node and one-node), Markov chain Mixed (White-box for structure, Grey-box for SH and DHW tanks, Black-box for ANN and Markov chain models) Nonlinear - 60 minutes Time-series ANN (for HP), Manufacturer data mentioned for HP specs, but detailed fit type not specified | Weather (solar radiation), SH demand, DHW demand ANN (feedforward), Markov chain 24 hours | Minimize operational electricity cost of the heat pump (HP) Hard only -- includes min/max temperature bounds for SH and DHW tanks, and a ±4 C limit on SH setpoint changes per time step SH tank temperature setpoint (continuous), DHW tank charging On/Off state (binary) |  |  |  |  | Measurement | No |  |  | 12 and 15
9 | Kurte et al. (2020) | 2020 | 1 | RL | Sustainability | Field site | Knoxville, Tennessee, USA | United States | North America | detached energy-efficient house | two-zone air-to-air conditioning with two-stage compressor and variable-speed fan | Whole building | Whole building | 223 | 5 | 3A | Cooling | High |  |  |  |  | Q-learning Resistance-Capacitance (RC) | HVAC on/off two | time, indoor temperature, outdoor temperature, and PV power four | minimizing HVAC energy use while maintaining comfort Boltzmann exploration | Simulation | No |  |  | 16
10 | Knudsen et al. (2021) | 2021 | 1 | MPC | Applied Energy | Laboratory | Trondheim, Norway | Norway | Europe | test house at a university | hydronic floor heating from a resistive-heated tank, with mechanical ventilation | Living Lab | Whole building | 102 | 14 | 6A | Heating | High | LP MATLAB linprog (dual-simplex) Not guaranteed | State-space model Linear 3 states 30 minutes - | Outdoor temperature, solar irradiation Weather API (Norwegian Meteorological Institute) and Solcast web service 48 hours | Cost minimization Mixed hard-soft (zone air temperature constraints with slack variables) Heat input |  |  |  |  | Simulation | No |  |  | 22.5
11 | Svetozarevic et al. (2022) | 2022 | 1 | RL | Applied Energy | Field site | Dübendorf, Switzerland | Switzerland | Europe | residential module in a sustainable demonstrator building | radiant heating with HP and emulated EV integration | Apartment bedroom | Subset of building | 17.6 | 5 | 5A | Heating | Low |  |  |  |  | Deep Deterministic Policy Gradient (DDPG) Recurrent Neural Network (RNN) for room temperature modeling and a simple linear model for the EV battery | room temperature control (valve position) and EV charging/discharging 1 (single continuous value) | time, indoor temperature, outdoor temperature, solar irradiance, and EV battery state-of-charge (SoC) 5 variables (one for each state) | minimize energy usage and comfort violations, with a penalty for temperature violations outside comfort bounds Boltzmann exploration | Measurement | No |  | 27
12 | Bünning et al. (2022) | 2022 | 4 | MPC | Applied Energy | Field site | Dübendorf, Switzerland | Switzerland | Europe | residential module in a sustainable demonstrator building | hydronic loop with HPs, variable-speed pump, room valves, and ceiling radiant systems | Two identical bedrooms within the apartment | Subset of building | 17.6 | Test 1: 41 days (258 baseline days) Test 2: 39 days (230 baseline days) Test 3: 41 days (184 baseline days) Test 4: 35 days (206 baseline days) Total: 156 days | 5A | Both | Low | QP (for ARMAX and RF), General convex (for ICNN) CVXOPT (QP), COBYLA (ICNN) Global (QP), Not guaranteed (COBYLA for ICNN) | ARMAX, Random Forest with linear regression, Input Convex Neural Network (ICNN) Linear (ARMAX), Mixed (ICNN), Mixed (RF with piecewise linear behavior) ARMAX uses δ = 3; exact number of states not specified 30 minutes - | Ambient temperature, global solar irradiation Weather service (MeteoSwiss), one-hour resolution (implied schedule) 6-7 hours | Minimize energy use (quadratic cost on control input) with soft penalties for comfort violations Mixed hard-soft (hard on control bounds, soft on comfort with slack variables) Valve position (on/off duty cycle via PWM), zone temperatures (predicted) |  |  |  |  | Measurement | No
13 | Vivian et al. (2022) | 2022 | 1 | MPC | Applied Thermal Engineering | Laboratory | Piacenza, Italy | Italy | Europe | laboratory building | air-to-water HP with fan coils, air extractors, and simulated PV panels | Whole building | Whole building | 59.4 | 5 | 4A | Both | Low | Mixed-Integer Quadratic Program (MIQP) Gurobi Not guaranteed | 5R3C lumped capacitance model Linear 3 states 15 minutes Polynomial fit | Weather (outdoor temperature, solar radiation), PV production External weather service, pvlib model for PV 24 hours | Cost minimization with penalty on control deviations Mixed hard-soft (comfort as soft, system constraints as hard) Heat pump on/off state, compressor frequency, circulation pump state, indoor air temperature, tank temperature, heat flows (to/from tank and space) |  |  |  |  | Measurement | No |  |  | 13.5
14 | Brown and Beausoleil-Morrison (2023a) | 2023 | 1 | MPC | Science and Technology for the Built Environment | Field site | Ottawa, Canada | Canada | North America | two-story research facility within a university | hydronic floor system for heating and cooling | Whole building | Whole building | 149 | 13 | 6A | Both | High | Full factorial evaluation (enumerative search) Custom Global (via exhaustive search of all control sequences) | Multiple linear regression (MLR) Linear - 30 minutes - | Indoor air temperature (Tia) MLR using current and past measurements (no external forecast) 4 hours | Multi-objective (minimize heating/cooling operation and maintain comfort) Mixed hard-soft On-Off States (heating and cooling pump operation) |  |  |  |  | Measurement | No |  | Reduction in heating hours: from 36.4 hours to 18.5 hours (49% reduction). Reduction in cooling hours: from 59.6 hours to 38.5 hours (35% reduction). Total: from 96 hours heating/cooling to 57 hours heating/cooling (40.6% reduction)
15 | Wang et al. (2023) | 2023 | 2 | MPC | Energy and Buildings | Field site | Shenzhen, China | China | Asia | two-room apartment with living room | forced-air with fixed-speed, single-stage mini-split air conditioners | Apartment room | Subset of building | 20 | 12 | 1A | Cooling | High | Mixed-Integer Linear Program (MILP) (due to binary on-off decisions and soft constraints) IPOPT via CVXPY Not guaranteed | First-order RC network Linear - 10 minutes - | Ambient temperature, solar irradiation External weather API (ALICloud) with interpolation 12 hours | Cost minimization (electricity cost under ToU pricing) Mixed hard-soft (soft comfort constraints, hard dynamics and binary control) On-off states of air conditioners (binary control input) |  |  |  |  | Measurement | No |  |  | 22.1 and 26.8
16 | Vallianos et al. (2023) | 2023 | 1 | MPC | Journal of Building Performance Simulation | Field site | Shawinigan, Québec, Canada | Canada | North America | two-story detached house with a basement | radiant heating with electric baseboards and smart thermostats | Whole Building | Whole building | 180 | 3 | 6A | Heating | High | Convex (LP or QP not explicitly specified) CVXPY (Python) - | RC network Linear 13th order (multi-zone model) 15 minutes - | Weather (outdoor temperature, solar irradiance) External weather forecast API (Solcast) 24 hours | Minimize electricity cost Mixed hard-soft (comfort enforced via soft constraints, heating capacity as hard constraints) Zone temperature setpoints |  |  |  |  | Measurement | No | 71 |  | 55
17 | Thorsteinsson et al. (2023) | 2023 | 4 | MPC | Applied Energy | Field site | Zealand, Denmark | Denmark | Europe | detached low-energy house | hydronic variable-speed air-to-water HP for space heating and domestic hot water | Whole building | Whole building | 230 | Comfort I-IV (I lowest, IV highest): I: 12 days II: 10 days III: 25 days IV: 50 days Total: 97 days | 5A | Heating | Low | MILP (Mixed-Integer Linear Program) + nonconvex components BONMIN via CasADi Not guaranteed | 2-state lumped RC network Linear 2 states (room air temperature, floor temperature) 5 minutes Polynomial fit for COP (nonlinear function of ambient temperature and power) | Weather (ambient temperature, solar radiation), Electricity price, PV output Weather service (Yr.no), Price API, regression for PV output 24 hours | Minimize electricity cost (including CO₂ emissions) and discomfort Mixed hard-soft Heat pump power, On/Off state, valve positions (binary), artificial ambient temperature (used to influence heat pump operation) |  |  |  |  | Measurement | No |  |  | Comfort I-IV (I lowest, IV highest): I: 32.8% (12 days) II: 29.1% (10 days) III: 17.4% (25 days) IV: 2.3% (50 days) Total: 97 days
18 | Brown and Beausoleil-Morrison (2023b) | 2023 | 1 | MPC | Applied Energy | Field site | Ottawa, Canada | Canada | North America | two-story research facility within a university | hydronic floor system for heating and cooling | Whole building | Whole building | 149 | 182 | 6A | Both | High | Enumerative search over all binary sequences Custom (brute-force evaluation of all pump sequences) Global (within evaluated options) | Multiple linear regression (MLR) Linear - 30 minutes - | Weather (GHI), Indoor air temperature (Tia) Persistent forecasting 4 hours | Minimize energy use and temperature violations Mixed hard-soft (temperature band with penalties) On/Off states of heating and cooling pumps |  |  |  |  | Measurement | No
19 | Yin et al. (2024) | 2024 | 1 | MPC | Applied Energy | Field site | Dübendorf, Switzerland | Switzerland | Europe | residential module in a sustainable demonstrator building | hydronic loop with HPs, variable-speed pump, room valves, and ceiling radiant systems | UMAR unit (three-room residential space) where each room is treated as a separate thermal zone | Subset of building | 155 | 5 | 5A | Heating | Low | QP OSQP Not guaranteed | State-space models identified from data (e.g., N4SID) and DeePC; physics-informed for BiLevel Linear 2 states per zone (inferred from SMM-PC implementation) 10 minutes - | Zone temperature, control inputs Data-driven via Hankel matrices (DeePC), state-space predictions (SMM-PC/N4SID) 6 hours | Minimize energy consumption while maintaining comfort Mixed hard-soft (temperature bounds with slack) Valve positions (control inputs), predicted zone temperatures |  |  |  |  | Simulation | No
20 | Jiang et al. (2024) | 2024 | 10 | MPC | Energy and Buildings | Field site | Home A Norman, OK Home B Miami, FL Home C Norman, OK Home D Norman, OK Home E Norman, OK Home G Norman, OK Home I Norman, OK Home J Norman, OK Lab House Norman, OK | United States | North America | nine single-family houses | central forced-air systems with ACs designed for cooling | Whole building Subset of building | Whole building Subset of building | Home A 222.97 Home B down 144.00 Home C down 199.74 Home C up 130.06 Home D 232.26 Home E 143.10 Home G 167.23 Home I 241.55 Home J 199.74 Lab House 154.03 | Home A 15.00 Home B down 20.00 Home C down 5.00 Home C up 5.00 Home D 6.00 Home E 6.00 Home G 2.00 Home I 20.00 Home J 10.00 Lab House 24.00 | 3A 1A | Cooling | High | MILP - Not guaranteed | Second-order RC-based gray-box model Linear 2R2C (2 states for the home thermal model) 5 minutes - | Weather (outdoor temperature, solar irradiation, wind speed), TOU rate Weather forecast (not specified method), TOU rate (assumed) 12 hours | Cost, Energy flexibility Mixed hard-soft (with soft constraints on temperature) AC on/off states, indoor temperature, slack variables for temperature deviation |  |  |  |  | Measurement | No |  |  | Home A 39.00 Home B down 31.51 Home C down -13.49 Home C up 10.06 Home D 87.06 Home E 23.60 Home G 46.82 Home I 33.53 Home J 32.05 Lab House 27.05
21 | Pergantis et al. (2024a) | 2024 | 1 | MPC | Applied Energy | Field site | West Lafayette, IN | United States | North America | detached full-electric single-family home | forced-air variable-speed air-to-air HP with staged electric resistance backup heating | Whole building | Whole building | 208 | 33 | 5A | Heating | High | Convex optimization (formulated for use with convex solvers) CVX toolbox (MATLAB) Global | RC network Linear One-state model 60 minutes Manufacturer data (COP fitted using manufacturer data), convex reformulation of electric power model | Weather, Internal gains Support Vector Machine (for internal gains), weather API (Oikolab) for outdoor temperature 24 hours | Multi-objective -- minimize energy use, cost, and peak demand while maintaining thermal comfort Mixed hard-soft -- includes equipment capacity limits and bounded comfort deviations Indoor temperature setpoint, HVAC thermal power, and electrical power input |  |  |  |  | Measurement | Yes |  |  | 28
22 | Shamachurn et al. (2024) | 2024 | 1 | MPC | Advanced Control for Applications: Engineering and Industrial Systems | Field site | Reduit, Mauritius | Mauritius | Africa | single-story, two-zone concrete building for tropical climate testing | forced-air with a portable AC, electric fan, and air extractors, with adjustable speed settings | 2 rooms of the building | Subset of building | 9 | 0.5 | 2A | Cooling | High | QP MATLAB MPC Toolbox (default solver) - | Linear state-space (identified using N4SID and refined with PEM) Linear Seventh-order 1 minute - | - - 1 hour | Minimize temperature tracking error Hard only (temperature bounds) Temperature setpoint (mapped to heating power / AC compressor ON/OFF) |  |  |  |  | Measurement | No
23 | Pergantis et al. (2024b) | 2024 | 2 | MPC | Building and Environment | Field site | West Lafayette, IN | United States | North America | detached full-electric single-family home | forced-air variable-speed air-to-air HP with staged electric resistance backup heating | Whole building | Whole building | 208 | 38 | 5A | Cooling | High | Convex (LP/QP unspecified) CVX (MATLAB) - | 2R1C RC network Linear Single-zone, 2 resistances and 1 capacitance 60 minutes Manufacturer data (COP and SHR curves) | Outdoor temperature, outdoor humidity, solar irradiance, wind speed, internal heat gains, wet-bulb temperature, SHR Gaussian Process Regression (wet-bulb), linear regression (SHR), support vector machine (exogenous load), weather service forecasts 24 hours | Multi-objective (Cost, Peak Demand, Comfort) Mixed hard-soft (capacity limits, temperature bounds with soft penalties) Indoor temperature set-points (sent to heat pump thermostat) Control Signal: Temperature set-point |  |  |  |  | Measurement | Yes |  |  | 24.55 and 2.5
24 | Pergantis et al. (2025) | 2025 | 1 | MPC | Applied Energy | Field site | West Lafayette, IN | United States | North America | detached full-electric single-family home | forced-air variable-speed air-to-air HP with staged electric resistance backup heating | Whole building | Whole building | 208 | 31 | 5A | Heating | High | MILP via transformation Gurobi (via CVX in MATLAB) Global (via MILP with duality gap <1%) | 2R1C thermal circuit model Model Linearity: Linear - 5 minutes Manufacturer data and polynomial fit for COP | Weather, Exogenous heat gains, Hot water draws, Uncontrolled electrical loads Support Vector Machine (SVM) with autoregressive error correction; nearest neighbors for hot water draws 12 hours | Multi-objective (Cost, Comfort, Peak current limit violations) Mixed hard-soft Temperature setpoints (HP, WH), HP thermal power, On-off states, Backup heat stage, Currents (HP, WH)

## commercial (papers)
| Paper | Year | # of tests | Control method | Publication venue | Field site or laboratory? | Location | Country | Continent | Building description | HVAC system | Controlled space | Whole building or subset of building? | Floor space (m2) | Test duration (days) | Climate zone | Heating, cooling, or both | Control action (high level vs low level) | Solver details (MPC) | System model (MPC) | Forecasting (MPC) | Optimization problem (MPC) | RL setup (RL) | Action space (RL) | State space (RL) | Learning objective (RL) | Benchmark | Confidence interval? | Electricity savings (%) | Thermal energy savings (%) | Cost savings (%)
1 | Henze et al. (2005) | 2005 | 1 | MPC | HVAC&R Research | Laboratory | Ankeny, IA, US | United States | North America | eight office rooms at a test facility | forced-air fixed-speed with air-cooled chillers, ice storage, and air handling units (AHUs) | 8 office rooms | Subset of building | 198.4 | 4 | 5A | Cooling | High | Nonconvex unspecified Quasi-Newton (passive), Dynamic Programming (active), implemented via MATLAB Not guaranteed | TRNSYS (building simulation) Nonlinear - 60 minutes Fixed COPs | Ambient temperature, relative humidity, global and direct solar radiation 30-day bin model 24 hours | Cost Hard only Zone temperature setpoints, TES charge/discharge rate |  |  |  |  | Simulation | No
2 | Liu and Henze (2006b) | 2006 | 1 | RL | Energy and Buildings | Laboratory | Ankeny, IA, US | United States | North America | eight office rooms at a test facility | forced-air fixed-speed with air-cooled chillers, ice storage, and AHUs | 8 office rooms | Subset of building | 198.4 | 6 | 5A | Cooling | High |  |  |  |  | Q-learning hybrid RL controller, combining both model-based and model-free control methods | Zone air temperature set-point, thermal storage charge rate 10x20 | Building mode, thermal storage charge state 3, 6 | cost minimization Epsilon-greedy | Simulation | No |  |  | 8.3
3 | Kolokotsa et al. (2009) | 2009 | 1 | MPC | Building and Environment | Laboratory | Chania, Crete, Greece | Greece | Europe | laboratory in a university building | forced-air heating and cooling via split-type air conditioning | Laboratory in the Technical University of Crete with high ceilings (3.5 m) | Subset of building | 125 | 2.7083 | 3A | Heating | Low |  | Bilinear model Nonlinear - 10 minutes (2 minutes during identification) - | - - 5 time steps (50 minutes) | Multi-objective (minimize deviation from setpoints and energy use) Mixed hard-soft Window opening, shading position, lighting level, HVAC heating/cooling output |  |  |  |  | Measurement | No
4 | Liao and Dexter (2010) | 2010 | 1 | MPC | IEEE Transactions on Control Systems Technology | Field site | Garston, England | England | Europe | office building with office, meeting rooms, and lecture theaters | radiant heating with thermostatic valves | Three types of rooms: offices, small meeting rooms and large lecture theatres | Whole building | 1350 | 45 | 4A | Heating | High |  | Discrete-time linear difference equation model (based on simplified physical model) Linear - 30 s (ON/OFF logic), 300 s (intermediate loop), 3600 s (outer loop) - | Outside air temperature, solar radiation - 1 hour (implied by outer loop sampling interval) | Energy Hard only Boiler ON/OFF state, supply water temperature setpoint |  |  |  |  | Simulation | No
5 | Prívara et al. (2011) | 2011 | 2 | MPC | Energy and Buildings | Field site | Prague, Czech Republic | Czech Republic | Europe | university building with seven control blocks | hydronic ceiling radiant heating with embedded beams, heat exchanger, and valve control | 1) Particular building blocks (B1 and B2) 2) Whole building consisting of 7 control blocks | Subset of building Whole building | 1) 7016.68 and 6646.17 2) 47830.06 | 45 45 | 5A | Heating | High | QP (Quadratic Programming) - - | State-space model (subspace identification) Linear - - - | Outside temperature Schedule-based (uses Tmin and Tmax as daily forecast bounds) - | Energy (and implicitly comfort) Mixed hard-soft Heating water setpoint (via valve control) |  |  |  |  | Measurement | No |  | 20.5 29 | _ 29
6 | Široký et al. (2011) | 2011 | 4 | MPC | Applied Energy | Field site | Prague, Czech Republic | Czech Republic | Europe | university building with seven control blocks | hydronic ceiling radiant heating with embedded beams, heat exchanger, and valve control | 1) B1 and B2 2) B1 3) B2 4) B3 | Subset of building | 1) 7016.68 and 6646.17 2) 7016.68 3) 6646.17 4) 7207.21 | 7, 49, 49, and 49 | 5A | Heating | High | QP Scilab internal QP solver Not guaranteed | RC network Linear 4-state model per block 20 minutes - | Weather (outdoor temperature), Room temperature reference schedule Weather from NOAA, reference schedule from BAS; no modeling method used 48 hours | Energy Mixed hard-soft Supply water temperature |  |  |  |  | Measurement | No |  | 16.24 B1: 28.74%, B2: 26.83%, B3: 17.67%
7 | Castilla et al. (2011) | 2011 | 8 | MPC | Energy and Buildings | Field site | Almeria, Spain | Spain | Europe | office space in a bioclimatic research facility | forced-air with variable fan speed and chilled water coils | Office room | Subset of building | 27.38 |  | 3B | Cooling | High | Nonlinear Programming (NLP) - Not guaranteed | First-order transfer function models identified using PRBS (pseudo-random binary signals) Linear First-order (one state) 5 minutes - | - | Energy (via control effort) and Thermal Comfort (PMV); Multi-objective Mixed hard-soft Indoor temperature (setpoint), Fan-coil velocity (fan speed) |  |  |  |  | Simulation | No
8 | Aswani et al. (2012) | 2012 | 1 | MPC | Proceedings of the IEEE | Laboratory | Berkeley, CA, US | United States | North America | ground-floor university building | forced-air, single-stage HP with single-speed operation | The controlled space is a computer laboratory located on the ground floor of a large engineering building on the Berkeley campus. Here are some specific details: Windows: It has external windows on its south and west walls. Equipment: The room contains 16 desktop computer workstations and two laser printers. Occupancy: The room's occupancy can peak at over 20 individuals, varying depending on the due dates of projects, assignments, and exams. HVAC System: The room has its own HVAC equipment, which allows for independent experiments without affecting other rooms in the building. | Subset of building | 59.46 | 3 | 3C | Cooling | High | QP SNOPT (via TOMLAB in MATLAB) Not guaranteed | RC network (discrete-time linear model inspired by Newton’s law of cooling) Linear - 15 minutes - | Weather, Occupancy (as internal gains) Weather via NOAA API; Occupancy inferred using residuals from model (simple estimation) 5 hours | Energy, Temperature Deviation (Multi-objective) Mixed hard-soft On-Off duty cycle (PWM-based control input) |  |  |  |  | Simulation | No | 47
9 | Ma et al. (2012a) | 2012 | 2 | MPC | IEEE Transactions on Control Systems Technology | Field site | Merced, CA, US | United States | North America | university building | forced-air centralized system with chillers, thermal energy storage, and distribution loops | Whole building | Whole building |  | 5 and 5 | 3B | Cooling | Low | NLP - Not guaranteed | RC model for building load; simplified hybrid model for plant including lookup tables and thermal tank dynamics Mixed Four-state model for thermal energy storage 60 minutes Lookup table (for chillers and fan coils) | Weather, Internal gains, Solar load Weather forecast (NOAA), schedule-based internal load prediction 72 hours (weather); 24 hours (control horizon) | Cost (electricity), Efficiency (COP) Mixed hard-soft Chilled water flow rate, Supply temp, Condenser water temp, On/Off states |  |  |  |  | Measurement | No
10 | Gayeski et al. (2012) | 2012 | 2 | MPC | HVAC&R Research | Laboratory | Atlanta, GA, US Phoenix, AZ, US | United States | North America | test chamber simulating office conditions with another climate chamber | thermally-activate building system (TABS) with radiant cooling by low-lift chilled water | Test chamber has dimensions of roughly 3.66 m by 5.18 m by 2.44 m. One test chamber representing a typical office zone with one exterior wall and another climate chamber used to simulate climate conditions outside the exterior wall. | Whole building | 18.958 | 7 | 3A 1B | Cooling | High | Nonconvex unspecified Generalized Pattern Search (GPS) Not guaranteed | Transfer function (CRTF), second-order model for chilled-water return temperature, regression-based chiller performance model Nonlinear Eighth-order for temperature CRTFs; second-order for chilled-water return temperature 30 minutes Polynomial fit (tri-cubic regression for chiller performance) | Outdoor temperature, internal gains, adjacent zone temperature Schedule 24 hours | Energy Mixed hard-soft Compressor speed, condenser fan speed |  |  |  |  | Measurement | No |  | 25 and 19
11 | Ferreira et al. (2012) | 2012 | 2 | MPC | Energy and Buildings | Field site | Algarve, Portugal | Portugal | Europe | four rooms in a university building | forced-air variable refrigerant flow (VRF) systems with ducted indoor and outdoor units per zone | 4 rooms (presumably office rooms) | Subset of building |  | 1- Exp 3 (summer): 2 days 2- Exp 4,5,6: 1 day | 3A | Cooling Heating | High | Discrete optimization using branch and bound Custom branch and bound algorithm Global (within discrete space) | Radial basis function (RBF) neural networks Nonlinear - 5 minutes - | Outside temperature, humidity, solar radiation RBF neural networks selected by multi-objective genetic algorithms (MOGAs) 2 to 4 hours | Energy (with thermal comfort constraint) Mixed hard-soft HVAC on/off states and temperature setpoints |  |  |  |  | Measurement | No | _ 57
12 | Bengea et al. (2014) | 2014 | 1 | MPC | HVAC&R Research | Field site | Champaign, IL, US | United States | North America | office building | forced-air with variable air volume (VAV) dual-duct multi-zone AHU | Office building | Whole building | 650.3 | 5 | 5A | Heating | High | NLP IPOPT Not guaranteed (local solution) | Semi-empirical component models and thermal zone models Nonlinear - Empirical correlations and thermal/mass balances (e.g., for fans, coils); polynomial-like behavior? | Weather, Occupancy, Internal gains NOAA online data for weather; historical occupancy sensor data for internal loads 3 hours | Energy Mixed hard-soft Supply flow rate, mixed air temperature, hot and cold deck discharge temperatures, zone supply temperatures |  |  |  |  | Measurement | No | 72.5
13 | West et al. (2014) | 2014 | 2 | MPC | Energy and Buildings | Field site | 1) Newcastle, Australia 2) Melbourne, Australia | Australia | Oceania | three-story office buildings | forced-air with AHUs, chillers, combined heat and power, and boilers | Whole building | Whole building | 1) 3322 2) 1808 | 25 and 5 | 3A | Heating | High | QP - - | Linear Time-Invariant (LTI) grey-box model using second-order transfer functions Linear - 5 minutes - | Weather (temperature, humidity), Internal loads (TBase), Occupant comfort feedback Schedule / Historic data (used for daily model refitting); weather forecasts mentioned Until end of current business day | Multi-objective (Energy, Cost, Occupant Comfort, Emissions) Mixed hard-soft Zone temperature set-points, supply air temperature set-points |  |  |  |  | Measurement | No | 14 _ | 19 32 | 16.9 _
14 | Castilla et al. (2014) | 2014 | 1 | MPC | Journal of Process Control | Field site | Almeria, Spain | Spain | Europe | office space in a bioclimatic research facility | forced-air with variable fan speed and chilled water coils | Office room | Subset of building | 27.38 | 15 | 3B | Heating | High | QP (via linearization of nonlinear model) - Not guaranteed (local solution through linearization at each sample time) | First-principles-based nonlinear thermal model Nonlinear - 8 minutes (lower layer), 240 seconds (upper layer) - | - - 15 steps (duration not explicitly converted to hours; likely 1-2 hours based on time step) | Thermal comfort (PMV ~ 0) and energy minimization Mixed hard-soft Impulse air temperature, indirectly controlling fan speed and water flow |  |  |  |  | Measurement | No | 53
15 | Váňa et al. (2014) | 2014 | 1 | MPC | Journal of Process Control | Field site | Hasselt, Belgium | Belgium | Europe | three-floor office building, underground garage and under-roof apartment excluded | hydronic ground-coupled HPs with TABS, AHUs, floor heating, and seasonal thermal storage | The controlled space in the study includes only the three office floors of the Hollandsch Huys building, divided into 12 thermal zones. The underground garage and under-roof apartment were not part of the controlled system. | Subset of building | 3760 | 25 | 4A | Heating | High | QP - - | RC network (grey-box state-space model derived from thermal circuit equations) Linear 8 states (3 zone air temperatures, 5 concrete core temperatures) 28 minutes - | Outside temperature, solar radiation, internal loads Weather forecasts from NOAA; internal gains estimated using occupant schedules 2 days (48 hours) | Energy Mixed hard-soft Heat fluxes into TABS, supply water temperature, mass flow rates |  |  |  |  | Measurement | No |  | 17.07
16 | Maasoumy et al. (2014) | 2014 | 2 | MPC | 2014 American Control Conference | Field site | Berkeley, CA, US | United States | North America | university building | forced-air variable-speed fans and variable frequency drives | Whole building | Whole building | 1309.9 | 30 min & 45 min | 3C | Cooling | High | NLP IPOPT Local | Nonlinear equations with fan power polynomial, heating/cooling equations based on thermodynamics Nonlinear - 60 minutes Polynomial fit for fan power; thermodynamic equations for heating/cooling | Electricity price, Outside temperature, Occupancy, Disturbances - 24 hours | Multi-objective (flexibility reward minus HVAC energy cost) Mixed hard-soft Air mass flow rate, Flexibility envelopes, Fan power |  |  |  |  | Measurement | No
17 | Preglej et al. (2014) | 2014 | 1 | MPC | Energy and Buildings | Laboratory | Graz, Austria | Austria | Europe | research facility simulating real-world conditions | forced-air with fans, coils, humidifiers, dampers, and filters | Air-handling unit controlling temperature and relative humidity in a supply air duct connected to a factory hall​ | Subset of building |  | 2.5 hr | 5A | Both | Low | QP MATLAB fmincon Not guaranteed | Fuzzy model (Takagi–Sugeno fuzzy model with local linear models) Mixed - - - | Weather (ambient temperature), Internal conditions (temperature and humidity) Schedule - | Energy Mixed hard-soft Supply air temperature, Steam mass flow rate, Fan speed |  |  |  |  | Measurement | No |  | 44
18 | Parisio et al. (2014) | 2014 | 2 | MPC | IFAC Proceedings Volumes | Field site | Stockholm, Sweden | Sweden | Europe | ground-floor university laboratory | forced-air ventilation, district radiator heating, and inlet coil cooling | Laboratory in the ground floor of the building | Subset of building | 80 | 2 days with high occupancy 2 days with low occupancy | 6A | Heating | High | Linear Programming (LP) - Not guaranteed | RC network Linear - 10 minutes - | Weather, Occupancy Scenario-based sampling from data 8 hours | Energy Mixed hard-soft Supply air temperature, Radiator temperature, Ventilation flow rate |  |  |  |  | Measurement | No
19 | Parisio et al. (2015) | 2015 | 1 | MPC | 53rd IEEE Conference on Decision and Control | Laboratory | Stockholm, Sweden | Sweden | Europe | ground-floor university laboratory | radiant heating via district-heated water radiators | laboratory room | Subset of building | 80 | 1 | 6A | Cooling | High | LP (via multiparametric programming reformulation) MPT toolbox (Multi-Parametric Toolbox) Global (within each polyhedral region) | Two-node RC network Linear Two states per zone (air temperature and wall temperature) 10 minutes - | Occupancy, Outdoor temperature, Solar radiation Scenario-based (sampled from learned distributions) 9 hours | Energy Mixed hard-soft Supply air temperature, Radiator temperature, Ventilation mass flow, Intermediate variables for heating/cooling airflow |  |  |  |  | Measurement | No |  | 32
20 | Goyal et al. (2015) | 2015 | 1 | MPC | Applied Energy | Field site | Gainesville, FL, US | United States | North America | office room in a university building | forced-air via AHU, with VAV terminal and reheat for zone control | Office room | Subset of building | 21.12 | 1 | 2A | Both | High | Nonconvex unspecified IPOPT Not guaranteed | Nonlinear RC network Nonlinear 14-state original model; reduced to 8 states via model reduction 10 minutes Polynomial fits (for fan power, conditioning power, and reheating power) | Outside air temperature, outside air humidity, solar radiation, occupancy Persistence (current value assumed constant over horizon) 3 hours | Energy Hard only Supply air temperature, supply air flow rate |  |  |  |  | Measurement | No | 40
21 | Zeng et al. (2015) | 2015 | 6 | MPC | Energy | Laboratory | Ankeny, IA, US | United States | North America | four office rooms at a test facility | forced-air with one AHU connected to multiple VAVs | All 6 cases focus on Zone A of the Energy Resource Station, consisting of 4 thermal zones served by AHU-A: East Room (EA), Interior Room (IA), South Room (SA), and West Room (WA). | Subset of building | 99.2 | 1 | 5A | Heating | High | Nonconvex unspecified Custom (Firefly Algorithm) Not guaranteed | Neural network (multi-layer perceptron) Nonlinear - 30 minutes - | Room temperature, relative humidity, HVAC energy consumption Neural network (MLP) 0.5 hours (next timestep prediction) | Energy Hard only Supply air temperature set point, Supply air static pressure set point |  |  |  |  | Simulation | No | Experiment 1 Case 1: 2.68% Case 2: 14.29% Case 3: 17.24% Experiment 2 Case 1: 2.23% Case 2: 10.3% Case 3: 16.94%
22 | Huang et al. (2015) | 2015 | 1 | MPC | Building and Environment | Field site | Adelaide, Australia | Australia | Oceania | one zone in the check-in hall of an airport | forced-air cooling with chillers, AHUs, and variable-speed pumps | Zone 1 of the check-in hall at Adelaide Airport's T1 building | Subset of building |  | 1 | 3B | Cooling | Low | LP YALMIP (solver interface) Not guaranteed | RC network + inverse neural network Mixed 2 states per zone (T_1, T_w) 10 minutes Simplified physical model (e.g., polynomial relationships and assumptions) | Weather (outdoor temperature), Occupancy (via CO₂), Electricity price Schedule-based (occupancy), Weather forecast (external source), TOU tariff (schedule) 6 hours | Cost Mixed hard-soft Cooling energy input, zone temperature trajectory, chilled water valve position, outdoor damper level |  |  |  |  | Measurement | No |  |  | 13
23 | Li et al. (2015) | 2015 | 1 | MPC | Science and Technology for the Built Environment | Field site | Philadelphia, PA, US | United States | North America | one-third of a medium-sized four-story office building | forced-air with three AHUs, VAVs with direct expansion cooling and gas boiler heating | ~1/3 of building (north side with four floors) | Subset of building |  | 20 | 4A | Cooling | High | NLP IPOPT Local | Low-order linear state-space models Linear Second-order (per zone) 3 minutes Polynomial fit | Weather (ambient temperature) - 2 hours | Energy Mixed hard-soft Supply airflow rate, SAT set-point, Reheat valve position |  |  |  |  | Measurement | No | 33
24 | Kim et al. (2015) | 2015 | 1 | MPC | Energy and Buildings | Field site | Knoxville, TN, US | United States | North America | basketball court within a gym | forced-air with four two-stage rooftop units (RTUs) | Basketball court within a gym affiliated with ORNL | Subset of building | 929 | 4 | 3A | Cooling | High | LP (relaxed from binary integer programming) - Not guaranteed | ARX (Auto-Regressive with Exogenous input) Linear ARX(2,2) 5 minutes - | Thermostat temperature ARX model with augmented disturbance states 1 hour | Energy, Peak Demand Hard only On-Off States (RTU stages) |  |  |  |  | Measurement | No | 8
25 | Sturzenegger et al. (2016) | 2016 | 4 | MPC | IEEE Transactions on Control Systems Technology | Field site | Allschwil, Switzerland | Switzerland | Europe | office building with five office floors and ground-floor kitchen and restaurant | hybrid system with AHU, TABS, gas boiler, dry cooling tower, and corner radiators | Whole building | Whole building | 6000 | 98 + 31 + 55 + 10 = 194 days | 4A | Cooling Heating Heating | High | Sequential Linear Programs (approximated bilinear program) CPLEX Not guaranteed (iterative linearization of a bilinear problem) | Bilinear RC network Mixed (Bilinear) Reduced from ~300 to 35 states 15 minutes - | Weather (temperature, solar radiation), Internal gains (occupancy, equipment) Kalman filter (weather), Schedule-based (internal gains) 58 hours | Cost Mixed hard-soft Supply air temp, airflow rate, blinds position (relaxed as continuous), lighting gains, heating/cooling inputs |  |  |  |  | Simulation | No
26 | De Coninck and Helsen (2016) | 2016 | 1 | MPC | Energy and Buildings | Field site | Brussels, Belgium | Belgium | Europe | two-story office building | hybrid system with air-source HPs, boiler, and hydronic loop | Whole building | Whole building | 960 | 15 | 4A | Heating | High | NLP IPOPT Not guaranteed (local solution using direct collocation) | RC network (grey-box thermal model with resistances and capacitances) Linear 4 states 5 minutes Polynomial fit (based on regression of efficiency curves) | Ambient temperature, plug loads (internal gains), occupancy Weekly persistence model for endogenous variables; adjusted weather forecast for ambient temperature 24 hours | Multi-objective (Energy Cost + Thermal Discomfort) Mixed hard-soft Thermal power of gas boiler, thermal power of each heat pump, total building heat consumption |  |  |  |  | Measurement | No |  | 25 | 37
27 | Ruano et al. (2016) | 2016 | 1 | MPC | Energy and Buildings | Field site | Faro, Portugal | Faro | Europe | three rooms in a university building | forced-air VRF system with air-cooled outdoor unit and ceiling-concealed indoor units | Room 2.12 was tested with IMBPC, while Rooms 2.11 and 2.13, controlled with standard temperature regulation, served as baselines for comparing energy savings, cost, and thermal comfort. | Subset of building | 131.25 | 6 hrs | 3A | Cooling | High | Discrete optimization Custom (Branch-and-Bound) Global (due to exhaustive Branch-and-Bound search over discrete space) | Radial Basis Function (RBF) Neural Network Nonlinear - 5 minutes Static model using estimated constants based on operational cases | Room temperature, room relative humidity, mean radiant temperature, weather (TA, HR, SR), occupancy (movement), economic cost RBF neural networks for climate and weather; schedule-based method for occupancy 4 hours | Cost Hard only (thermal comfort via PMV bounds) Air conditioning reference temperature (discrete values) |  |  |  |  | Measurement | No | 50
28 | Costanzo et al. (2016) | 2016 | 1 | RL | Sustainable Energy, Grids and Networks | Laboratory | Genk, Belgium | Belgium | Europe | laboratory space for energy testing | ductless air conditioner units with basic monitoring | living lab equipped with HVAC systems and sensors for real-world energy testing. | Subset of building | 61.62 | 16 | 4A | Cooling | High |  |  |  |  | Q-learning ANN | HVAC on/off two | Time, indoor temperature, outdoor temperature, solar irradiance, previous action five ? | Energy cost Epsilon-greedy |  | No
29 | Fabietti et al. (2016) | 2016 | 4 | MPC | IEEE Transactions on Smart Grid | Field Test | Lausanne, Switzerland | Switzerland | Europe | four office rooms in a university research lab | radiant heating with commercial electric heater with hot water radiators disabled | 4 office rooms | Subset of Building | 90 | 0.5 each | 4A | Heating | High | QP (Quadratic Programming) MATLAB’s quadprog - | Grey-box model (thermal model based on first principles and identified parameters) Linear - 15 minutes - | - - - | Grid services (frequency regulation) Mixed hard-soft HVAC power consumption |  |  |  |  | Simulation
30 | Vrettos et al. (2016) | 2016 | 6 | MPC | IEEE Transactions on Smart Grid | Laboratory | Berkeley, CA, US | United States | North America | thermally identical test cells in a research facility | forced-air with variable speed and dedicated AHUs | two thermally isolated test cells (60 m² each), designed to simulate commercial building environments | Subset of building | 60 | one day each | 3C | Cooling | Low | Nonconvex unspecified - - | RC network Linear - 15 minutes (MPC); 4 seconds (fan control); 1 day (reserve scheduling) Polynomial fit (fan model) | Ambient temperature, Solar radiation Forecast.io API (temperature), Clear-sky radiation model (solar) 1 day ahead | Multi-objective (comfort, energy, reserve capacity) Mixed hard-soft Air flow rate, Fan speed, Zone temperature |  |  |  |  | Measurement
31 | Gorecki et al. (2017) | 2017 | 10 | MPC | Energy and Buildings | Field site | Lausanne, Switzerland | Switzerland | Europe | five offices in an office building | electric heaters with direct modulation | 5 office rooms | Subset of Building | 115 | 1 each | 4A | Heating | Low | QP - Not guaranteed | ARX Linear Second-order per zone 15 minutes - | Weather, AGC signal Weather service for weather; time-series correlation for AGC 6 to 24 hours | Grid Services (Frequency Regulation) Mixed hard-soft Heater power input (PWM ratio), Intraday baseline adjustment |  |  |  |  | Simulation
32 | Schmidt et al. (2017) | 2017 | 3 | 2 MPC, 1 RL | Energy and Buildings | Field site | Granada, Spain | Spain | Europe | three-story school | hydronic heating with biomass boiler serving multiple circuits | Whole building | Whole building |  | 43 | 3A | Heating | High | Nonconvex unspecified Genetic Algorithm (for MPC-style), Custom RL (Fitted Q-Iteration) Not guaranteed | Neural network (Bayesian Regularized Neural Networks), Reinforcement Learning (Fitted Q-Iteration) Nonlinear - 15 minutes - | Outdoor air temperature, humidity, wind speed External forecast input + neural network correction One time step (15 minutes) | Multi-objective (minimize energy, improve comfort) Mixed hard-soft Supply temperature set-points | Q-learning - | Flow temperature set-points 3x3 ? | Time, indoor temperatures, water temperatures, outdoor temperature forecast over prediction horizon - | Energy cost Gaussian action noise | Measurement | No |  | 33
33 | Stauffer et al. (2017) | 2017 | 2 | MPC | Energy Procedia | Field site | Neuchâtel, Switzerland Winterthur, Switzerland | Switzerland | Europe | conference room and office building | forced-air with AHUs, radiators, and rotating heat exchanger | 1st: 70-seat conference room 2nd: Whole building | Subset of building Whole building | 1st: 120 2nd: 2100 | 1st: 38 2nd: 10 | 4A / 5A | Cooling Heating | High |  | Adaptive model (nonlinear predictive function) Nonlinear - - Operational cost estimated via Mollier chart and AHU component cost functions | Weather External national weather forecasting service - | Cost Mixed hard-soft Pulsed air temperature, air flow rate |  |  |  |  | Measurement | No |  |  | 22 _
34 | Hilliard et al. (2017) | 2017 | 1 | MPC | Building and Environment | Field site | Halifax, Canada | Canada | North America | five-story university building | forced-air with VAV reheat, HPs, district heating, and rooftop cooling tower | Whole building | Whole building | 10000 | 113 | 5A | Heating | High | Genetic algorithm for MPC search (nonconvex, unspecified) Custom (genetic algorithm) Not guaranteed | EnergyPlus (morning start), Random Forest regression (daytime) - - 15 minutes Simulated via EnergyPlus; simplified model output = whole building electrical and thermal loads | Weather (ambient temp, humidity, solar radiation) Schedule (for occupancy); measured or simulated weather inputs 2 hours (8 timesteps) | Energy Mixed hard-soft Zone air temperature (ZAT) setpoints |  |  |  |  | Measurement | Yes | 29 | 63
35 | Killian and Kozek (2018) | 2018 | 1 | MPC | Energy and Buildings | Field site | Salzburg, Austria | Austria | Europe | two floors of a five-story university office building | hybrid system with TABS (radiant) and fan coils (forced-air) | A total of 500 rooms in 2 floors of the building | Subset of building | 13000 | 49 | 5A | Heating | High |  | Takagi-Sugeno (TS) fuzzy model with local linear ARX models (LoLiMoT algorithm) Nonlinear State-space models of order 5 per local model - - | Weather (ambient temperature, solar radiation), Occupancy Schedule (for occupancy), Weather forecast provider (for weather) - | Energy (minimize control effort) Hard only Supply temperature to TABS and Fan Coils |  |  |  |  | Simulation | No
36 | Zhuang et al. (2018) | 2018 | 1 | MPC | Building and Environment | Field site | Sichuan Province, China | China | Asia | six above-ground floors of a shopping mall | forced-air with chillers, variable speed drivers, AHUs, and fan coils | 6 floors above ground | Whole building | 30750 | 1 | 3A | Cooling | High |  | Transfer function model using step response and PSD methods Linear Sum of first- and second-order transfer functions 30 seconds - | Outdoor temperature, solar radiation Weather forecast (sinusoidal approximation for temperature, empirical equation for solar radiation) - | Energy Hard only Supply chilled water temperature |  |  |  |  | Measurement | No | 16
37 | Michailidis et al. (2018) | 2018 | 1 | RL | Applied Energy | Field site | Aachen, Germany | Germany | Europe | three conference rooms in a university research building | hybrid forced-air and radiant system with concrete core and air chillers | three conference rooms (Room019, Room020, and Room021), while two other rooms (Room017 and Room018) were used for benchmarking. | Subset of building | 93 | 5 | 5A | Heating | High | [8 empty] | Measurement | No | 34.7 | 34.7
38 | Lindelöf et al. (2018) | 2018 | 1 | MPC | Energy Procedia | Field site | Sargans, Switzerland | Switzerland | Europe | three zones within an office building | hydronic system with oil-fired boiler | Subset of Building. Only managed 3 of the 4 heating circuits (1840 mw of the 2700m2 total) as the 4th was deemed to not need optimization | Subset of Building | 1840 | 46 | 4A | Heating | High |  | Neural network Nonlinear - - - | Weather - - | Energy - - Supply temperature (indirectly controlled) |  |  |  |  | Measurement | Yes |  | 31.9
39 | Viot et al. (2018) | 2018 | 1 | MPC | Energy and Buildings | Field site | Bordeaux, France | France | Europe | conference room in a university building | radiant underfloor heating with AHU and fan coil unit for ventilation and backup heating | Open-plan conference room | Subset of building | 200 | 30 | 3A | Heating | High |  | RC network (5R4C model) Linear - 10 minutes - | Weather, Occupancy, Internal gains (solar, occupants, AHU) Schedule + measured data 24 hours | Energy, Comfort (Multi-objective) Mixed hard-soft Water supply temperature (continuous) |  |  |  |  | Simulation | No |  | 35
40 | Granderson et al. (2018) | 2018 | 4 | MPC | Energy and Buildings | Field site | Long Beach, CA, US Dayton, OH, US New York, NY, US Washington, D.C., US | United States | North America | office, courthouse, hospital, and high school buildings | forced-air variable frequency drive systems | Whole building | Whole building | 15608 15621 27871 21832 | 170 108 113 148 | 3C / 4A / 4C | Cooling | High |  | Grey-box model - - - - | Weather, Building load - 24 hours | Energy - Supply air temperature, Duct static pressure |  |  |  |  | Measurement | No | 1.4, 8.9, -0.4, 1.9
41 | Joe et al. (2018) | 2018 | 1 | MPC | Energy and Buildings | Field site | West Lafayette, IN, US | United States | North America | open-plan office space in a university research building | hydronic radiant floor cooling, air-cooled chiller assumed | One open-plan office space (living lab 1) | Subset of building | 103.95 | 11 | 5A | Cooling | High | Convex optimization (quadratic, using biquadratic polynomials and linear constraints) MATLAB with Fmincon (active-set algorithm for system ID) Not guaranteed (convergence of PJ-ADMM) | Grey-box RC network (state-space model with lumped thermal parameters) Linear 17 states and 27 resistances (17C27R) in integrated model 30 minutes Polynomial fit (chiller performance modeled using biquadratic and quadratic polynomial curves from EnergyPlus reference) | Weather (outdoor temperature, humidity, wind speed, cloud cover), Internal gains (occupants, equipment, lighting) Schedule-based for internal gains; deterministic regression model for solar irradiance using NOAA data and literature coefficients 24 hours | Energy (electricity consumption of air-cooled chiller) Mixed hard-soft (hard constraints on temperature bounds; soft convergence via regulation term) Part Load Ratio (PLR) of chiller (cooling rate trajectory per floor section) |  |  |  |  | Simulation | No | 27
42 | Kim and Braun (2018) | 2018 | 2 | MPC | Energy and Buildings | Both | West Lafayette, IN, US FL, US | United States | North America | conference room in a university building and a retail store | forced-air systems with packaged RTUs | single conference room Whole building (retail store) | Subset of building Whole building | 105 1400 | 3 60 | 4C | Cooling | High | MILP - - | RC network with lumped output disturbance model Linear - 5 minutes Rated power used | Thermostat temperatures State-space model with disturbance estimation 0.5 to 1 hour | Energy, Peak Demand, Comfort (multi-objective) Mixed hard-soft On-Off states of RTU stages |  |  |  |  | Measurement | No | 12.95 and 14
43 | Joe and Karava (2019) | 2019 | 5 | MPC | Applied Energy | Field site | West Lafayette, IN, US | United States | North America | three open-plan office spaces in a university research building | radiant floor system in the first office, forced-air systems in the others | Three open-plan office spaces (living labs 1, 2, and 3) | Subset of building | 103.95 | 10 | 5A | Cooling Heating | Low | QP (cooling), LP (heating) MATLAB's quadprog (cooling), linprog (heating) Global | Grey-box state-space model Linear Five states (Tcav, Troom, Tsur, Tso, Tsi) 30 minutes (implementation), 5 minutes (simulation) Polynomial fit (air-cooled chiller), Vector representation (boiler) | Weather (outdoor temperature, solar radiation), Internal gains (occupancy, equipment), Electricity price Schedule (internal gains), NOAA weather forecast model with solar irradiance regression 24 hours | Cost (cooling), Energy (heating) Hard only Cooling/heating rate (via Part Load Ratio), water flow through radiant system |  |  |  |  | Both | No | 16 ¦ 35 ¦ (52+64)/2 ¦ _ ¦ 29 | 7.8 ¦ 18 ¦ _ ¦ 16 ¦ _ | 34 ¦ 50 ¦ (70+78)/2 ¦ _ ¦ _
44 | Lee et al. (2019) | 2019 | 1 | MPC | Energy and Buildings | Field site | West Lafayette, IN, US | United States | North America | open-plan office space in a university research building | hydronic radiant floor cooling, air-cooled chiller assumed | One open-plan office space (living lab 1) | Subset of building | 103.95 | 19 | 5A | Cooling | High | QP MATLAB quadprog Not guaranteed (solver fallback used when infeasible) | Grey-box RC network (state-space formulation) Linear 33 capacitances, 64 resistances (33C64R) 30 minutes Polynomial fit using EnergyPlus reference model (Trane CGAM20) | Weather (outdoor temperature), Occupancy, Internal gains (equipment, lighting, people) Schedule-based 24 hours | Energy (electricity consumption of chiller) Mixed hard-soft Chiller part-load ratio (PLR), cooling rates per zone |  |  |  |  | Measurement | No
45 | Zhang et al. (2019) | 2019 | 1 | RL | Energy and Buildings | Field site | Pittsburgh, PA, US | United States | North America | single-level office building | radiant heating system integrated with window mullions | Whole building | Whole building | 600 | 78 | 4A | Heating | High |  |  |  |  | Actor-critic EnergyPlus | Supply water temperature set-point 10 | Time, weather, indoor temperature, occupancy hundreds | Energy, PPD Entropy-based stochastic exploration | Measurement | No |  | 16.7
46 | Yang et al. (2019) | 2019 | 2 | MPC | Energy and Buildings | Laboratory | Singapore | Singapore | Asia | experimental cells in a building performance test faci | hybrid system with active chilled beams and primary AHU-induced mixing | test cell | Subset of building | 43.5 | 1 | 0A | Cooling | High | QP - - | Linear state-space model based on RC network Linear - 5 minutes Polynomial fit (linear empirical equations based on data fitting) | Weather, Internal heat gains - 1 hour (12 steps × 5-minute intervals) | Multi-objective (minimize cooling power and PMV deviation) Mixed hard-soft Cooling power of FCU, PAU, and chilled beams |  |  |  |  | Measurement | No | 14.7 and 20
47 | Yang et al. (2020a) | 2020 | 2 | MPC | Applied Energy | Field site | Singapore | Singapore | Asia | single lecture room in a university building | forced-air VAV with central plant and dedicated outdoor air system | Single room of building (Lecture Theatre 3) | Subset of building | 255 | 14 | 0A | Cooling | High | QP - - | RC network Linear - 2 minutes Polynomial fit | Occupancy, Internal gains, Weather (outdoor temperature and humidity) - 1 hour | Multi-objective (energy + thermal comfort) Mixed hard-soft Cooling power setpoints for AHU and DOAS |  |  |  |  | Measurement | Yes | 16 and 18
48 | Cotrufo et al. (2020) | 2020 | 1 | MPC | Energy and Buildings | Field site | Varennes, Québec, Canada | Canada | North America | single-story building with workstations and meeting rooms | forced-air with electric boiler for heating and natural gas boilers as backup | Whole building | Whole building |  | 70 | 6A | Heating | High | - implemented in MATLAB - | Gaussian Process Regression (GPR) Nonlinear - 60 minutes - | Weather (outdoor air temperature) Weather forecast data (external source) 24 hours | Natural gas consumption Hard only Indoor air temperature set-point |  |  |  |  | Measurement | Yes |  | 22.2
49 | Drgoňa et al. (2020) | 2020 | 1 | MPC | Journal of Process Control | Field site | Hasselt, Belgium | Belgium | Europe | three-floor office building, underground garage and under-roof apartment excluded | hybrid radiant and forced-air system with TABS and ground-source HP | The controlled space in the study includes only the three office floors of the Hollandsch Huys building, divided into 12 thermal zones. The underground garage and under-roof apartment were not part of the controlled system. | Subset of building | 3760 | 35 | 4A | Both | High | QP (for MPC); NLP (for post-processing actuator mapping) Gurobi (QP), MATLAB fmincon (NLP) QP -- Global; NLP -- Local | Linear state-space model (discretized LTI); derived from nonlinear Modelica (IDEAS) model Linear 700 states, 12 outputs, 21 inputs, 301 disturbances 15 minutes - | Weather, Occupancy, Internal gains, Solar radiation, Ambient and ground temperature Weather from Dark Sky API; occupancy and internal gains from stochastic schedule model 24 hours | Energy, Thermal comfort (multi-objective) Mixed hard-soft Heat flows (TABS, floor heating), zone temperatures, slack variables, actuator setpoints |  |  |  |  | Measurement | No | 53.5
50 | Yang et al. (2020b) | 2020 | 2 | MPC | Applied Energy | Field site | Singapore | Singapore | Asia | office and lecture theater in a multi-story institutional building | forced-air with ceiling-mounted VAV and external fan coil unit | 1) Office at level 3 of the Research Techno Plaza (RTP) building in NTU. The office is surrounded by adjacent air-conditioned spaces including offices, corridor and atrium. 2) Lecture theatre in NTU. | Subset of building | 46 255 | 10 | 0A | Cooling | High | NLP Hybrid approach (Exhaustive Search + SQP via MATLAB) Not guaranteed | Neural network (NARX-based ANN) Nonlinear - 5 minutes - | - - 1 hour | Multi-objective (minimize energy and thermal discomfort) Mixed hard-soft Cooling power (Qsa or Qcw) |  |  |  |  | Measurement | Yes | 36.7 | 58.5
51 | Chen et al. (2020) | 2020 | 1 | RL | Frontiers in Built Environment | Field site | Pittsburgh, PA, US | United States | North America | conference room in a university building | forced-air VAV with variable-speed airflow | Conference room | Subset of building | 20 | 21 | 4A | Cooling | Low |  |  |  |  | Gnu-RL Linear state-space | Supply air flow set-point - | Zone air temperature - | Quadratic state + action Gaussian action noise | Measurement | No |  | 16.7
52 | Freund and Schmitz (2021) | 2021 | 1 | MPC | Building and Environment | Field site | Hamburg, Germany | Germany | Europe | large government office building | radiant heating with district hot water | Whole building | Whole building | 2270 | 90 | 5A | Heating | High | NLP MATLAB fmincon Local | RC network (R7C4 gray-box model) Nonlinear 4 states per zone 30 minutes - | Weather, Occupancy, Internal gains Schedule, Weather forecast (MOSMIX), Historical data profile 48 hours | Multi-objective (Energy and Thermal Discomfort) Mixed hard-soft Supply temperature setpoints |  |  |  |  | Measurement | No |  | 30
53 | Sampaio et al. (2021) | 2021 | 2 | MPC | Energy and Buildings | Field site | Brussels, Belgium | Belgium | Europe | five-floor building | forced-air with central heating, cooling equipment, and AHUs | Whole building | Whole building | 25000 | 10 days cooling 17 days heating | 4A | Heating and Cooling | High | Nonconvex unspecified NSGA-II (for calibration), NOMAD (for control optimization) Not guaranteed | RC network (R6C2 model) Linear 6 resistances, 2 capacitances 15 minutes - | Indoor temperature, thermal power Simulation using calibrated RC model 1 day | Energy Hard only Day initial time, Night set-point temperature (heating only), Night initial time |  |  |  |  | Simulation | No |  | 8.6% cooling and 11.7% heating
54 | Yang et al. (2021) | 2021 | 3 | MPC | Applied Energy | Laboratory | Singapore | Singapore | Asia | experimental cells in a building performance test faci | hybrid system with active chilled beams and primary AHU-induced mixing | test cell | Subset of Building | 43.5 | 2 - 2 - 1 | 0A | Cooling | Low | QP (dynamic optimizer); static optimization via bisection method. - - | Linear state-space model (SSM) for thermal dynamics; hybrid model (physics + data-driven) for visual comfort and lighting power Linear - 5 minutes - | Weather (solar irradiance), internal gains (from occupancy, lighting) Measured values used as inputs; no separate forecasting model 1 hour | Multi-objective (minimize cooling energy, lighting energy, and thermal discomfort). Mixed hard-soft. Chilled water valve positions, pump speed, EC window tint level. |  |  |  |  | Measurement | No | 18.4 - 22.2 - 23.8
55 | Touzani et al. (2021) | 2021 | 3 | RL | Applied Energy | Laboratory | Berkeley, CA, US | United States | North America | office room in a controlled test facility | forced-air with variable-capacity AHU, shared chiller, PV, and battery | Office room with a large south-facing window | Subset of building | 57 | 7 | 3C | Cooling | High |  |  |  |  | Deep Deterministic Policy Gradient (DDPG) Model-free RL using simulation (EnergyPlus + Modelica) | Supply air temperature set-point, supply air flow set-point, battery charge/discharge power set-point 3 (continuous) | Time, weather, HVAC power, PV power, battery SoC, energy price forecast Continuous multidimensional vector ~ 6-8 features ? | Energy, temperature penalty, battery SoC penalty Ornstein–Uhlenbeck process | Measurement | No |  |  | EE: 0.6 % Shed: 29.4 % Shift: 39.6 %
56 | Jung et al. (2022) | 2022 | 5 | RL | Building and Environment | Laboratory | Seoul, South Korea | South Korea | Asia | climate chamber in controlled environment | NR | climate chamber (2.8 m × 3.9 m × 2.4 m) with controlled temperature, humidity, and air velocity, replicating a typical indoor environment with a desk and chair. | Subset of building | 10.92 | 30 min per each temp test | 4A | Both | High |  |  |  |  | Model-based CNN | Indoor temperature change - | Indoor temperature, occupant skin temperature/heart rate - | Energy, PPD - | Measurement | No
57 | Arroyo et al. (2022) | 2022 | 3 | MPC | Buildings | Laboratory | Heverlee, Belgium | Belgium | Europe | unoccupied test room in a research facility | radiant heating via TABS, supplied by an electric boiler | small, unoccupied test module | Subset of Building | 6.21 | 69 - 60 - 57 | 4A | Heating | Low | NLP JModelica with CasADi (direct collocation) Not guaranteed (local solution) | White-box: Modelica (IDEAS library); Grey-box: RC network (5R3C); Black-box: State-space White-box: Nonlinear; Grey-box: Linear; Black-box: Linear White-box: 94 states; Grey-box: 3 states; Black-box: 3 states 15 minutes White-box: Physics-based (Modelica components); Grey-box: Polynomial fit (quadratic); Black-box: Polynomial fit (quadratic) | Weather (ambient temperature, solar irradiation, dew point, wind speed, pressure, humidity), Electricity price External weather forecast service (DarkSky); electricity price from historical day-ahead market data 48 hours | Multi-objective (operational cost and thermal discomfort) Mixed hard-soft Valve opening position (affects supply temperature) |  |  |  |  | Measurement | No
58 | Kim and Braun (2022) | 2022 | 2 | MPC | Energy and Buildings | Field site | West Lafayette, IN, US | United States | North America | conference room in a university building | forced-air with packaged RTUs | One conference room | Subset of building | 105 | 5 and 15 | 5A | Cooling | High | MILP - - | RC network with lumped disturbance modeling Linear - 5 minutes (LMPC), 30 minutes (UMPC) - | Outdoor air temperature, Electricity price NOAA API for weather; fixed TOU schedule for price 12 hours (UMPC), 40 minutes (LMPC) | Cost, Peak Demand Mixed hard-soft Compressor stages (unit ON/OFF states) |  |  |  |  | Measurement | No |  |  | 3.61 and 8.67
59 | Blum et al. (2022) | 2022 | 1 | MPC | Applied Energy | Field site | Berkeley, CA, US | United States | North America | two office floors with closed offices below and open offices above | forced-air underfloor system with direct expansion cooling and heating | Two office spaces | Subset of building | 6038 | 31 | 3C | Both | Low | NLP IPOPT (via JModelica/Optimica) Local | RC network (R2C2) Linear - 10 minutes Polynomial fit (fan and compressor power modeled using polynomial expressions) | Weather (temperature, solar irradiance), Internal gains (plug load) k-NN for solar; average-by-hour-of-week for plug loads 24 hours | Energy Mixed hard-soft Supply air temperature, Supply fan speed, Compressor signal, Outside air fraction, Hot water valve position |  |  |  |  | Measurement | No | 40
60 | Naug et al. (2022) | 2022 | 1 | RL | IEEE Conference on Control Technology and Applications | Field site | Nashville, TN, US | United States | North America | three-story, energy-efficient mixed-use building | forced-air with a dedicated outdoor air system, VRF, and dual AHUs | Whole building | Whole building | 2958.776 | 365 | 4A | Both | High |  |  |  |  | Actor-critic ANN | AHU supply air tempearture set-point - | Weather, energy, AHU supply temperature Multi-dimensional | Energy consumption, temperature deviation, fan switching penalty Epsilon-greedy | Measurement | No | 14.3 | Cooling: 13.1
61 | Kim et al. (2022) | 2022 | 1 | MPC | Applied Energy | Field site | Merced, CA, US | United States | North America | central cooling plant at a university | forced-air with chilled water, thermal storage, PV, and flexible chillers | Whole building | Whole building |  | 7 | 3B | Cooling | Low | MILP GLPK Global | Discrete-time linear thermal network (1D RC model) for TES; linear regression for plant power Linear - 60 minutes Polynomial fit using historical data for plant power vs. mode and temperature | Outdoor temperature, PV generation, campus cooling load, non-plant electrical load, grid emission rate ANN (Artificial Neural Network) for cooling load and non-plant load; pvlib for PV; API for weather and MOER 48 hours | Multi-objective (minimize net emissions, peak demand, and SOC violations) Mixed hard-soft Plant mode (on/off), primary water flow rate setpoint, chiller load, SOC |  |  |  |  | Measurement | No
62 | Zhang et al. (2022) | 2022 | 1 | MPC | Advances in Applied Energy | Field site | Blue Lake Rancheria, CA, US | United States | North America | gas station convenience store | forced-air RTUs with refrigeration, freezer, battery, and PV integration | Whole building | Whole building | 418 | 365 | 4C | Both | High | NLP IPOPT (via JModelica.org and CasADi) Local | Lumped RC network Linear Fourth-order (one state per zone: east, west, refrigerator, freezer) 5 minutes Manufacturer data (nominal capacity and efficiency used; no performance maps) | Outdoor temperature, Solar radiation, Internal heat gains Third-party weather service (DarkSky) + empirical solar radiation model + assumed constant internal gains 24 hours | Cost (energy + demand), Demand Response Mixed hard-soft Zone temperature setpoints (east, west, refrigerator, freezer), Battery charge/discharge power |  |  |  |  | Measurement | No |  |  | 11.7
63 | Maddalena et al. (2022) | 2022 | 1 | MPC | Energy and Buildings | Field site | Campo Grande, Brazil | Brazil | South America | operating and waiting rooms in a hospital | forced-air cooling with AHUs and variable-speed chiller | 2 operating rooms (OR) and 1 waiting room (WR) in the opthalmology section | Subset of building |  | 4 | 1A | Cooling | Low | Nonconvex unspecified IPOPT (via CasADi) Not guaranteed | Gaussian Process (non-parametric, Bayesian regression) Nonlinear Auto-regressive; includes current and past values (e.g., up to 3 past steps for each signal) 10 minutes Polynomial fit (ridge regression for chiller model) | Indoor temperature Gaussian Process (auto-regressive modeling) 2 hours | Energy Mixed hard-soft Valve positions (chilled water flow control) |  |  |  |  | Simulation | No
64 | Lei et al. (2022) | 2022 | 1 | RL | Applied Energy | Field site | Singapore | Singapore | Asia | office in a net-zero university building | hybrid system with dedicated outdoor air system and variable-speed ceiling fans | One office space | Subset of building | 164 | 10 | 0A | Cooling | Low |  |  |  |  | Q-learning Modelica Buildings Library | Room temperature, fan speeds 7x6x6x6 | Time, weather, occupancy, fan speed, indoor temperature - | Energy, temperature penalty Gaussian action noise | Measurement | No | 14
65 | Luo et al. (2022) | 2022 | 2 | RL | Applied Energy | Field site | US | United States | North America | university and mixed-use commercial buildings | hybrid system with chiller plant, AHUs, fan coils, and central air distribution | Whole building | Whole building |  | 90 |  | Cooling | Low |  |  |  |  | BCOOLER (policy iteration) ANN | Supply temperatures, flows, on/off states 12 | Temperatures, flows, on/off states 50 | Energy (s.t. action constraints) - | Measurement | No | 9 and 13
66 | Zhan et al. (2023) | 2023 | 1 | MPC | Energy and Buildings | Field site | Singapore | Singapore | Asia | six-zone office space in a net-zero energy building | forced-air with two fan coil units and individual zone VAVs | 6-zone office spaces located on level 5 | Subset of building | 320 | 49 | 0A | Cooling | High | QP IPOPT Not guaranteed | RC network Linear - 15 minutes - | Outdoor temperature, solar irradiance, PV generation, plug load LSTM (for weather), regression (for PV), persistent model (for plug load) 1 hour | Multi-objective (maximize PV self-consumption, maintain comfort) Mixed hard-soft Supply airflow rate per zone, optionally supply air temperature |  |  |  |  | Simulation | No
67 | Zhang et al. (2023) | 2023 | 2 | MPC | Energy and Buildings | Field site | West Lafayette, IN, US | United States | North America | two identical adjacent private office spaces | forced-air with individual VAV boxes and centralized AHU with reheat | Two identical, adjacent private office rooms. One exterior wall with 54% windows with movable shades. | Subset of building | 12.21 | 1 day in October, 1 day in January | 5A | Both | High | Nonlinear (due to energy cost function) Sequential Quadratic Programming (SQP) Not guaranteed | State-space model Linear 4 states total (2 air temps + 2 thermal mass temps) 30 minutes Polynomial fit based on EnergyPlus references | Solar gains, outdoor air temperature Weather forecast (NOAA), model-based solar gain estimation 12 hours | Energy Hard only Heating/cooling rate per zone |  |  |  |  | Measurement | No |  | 28 and 35
68 | Yue et al. (2023) | 2023 | 1 | MPC | Energy and Buildings | Field site | Zhejiang province, China | China | Asia | three-floor airport terminal | forced-air with air-cooled HPs, chilled water pumps, and AHUs | Whole Building | Whole building | 16500 | 15 | 3A | Cooling | High | Discretized optimization (Branch and Bound for cooling; Exhaustive search for sequencing) Custom (not a standard solver) Not guaranteed | Hybrid model (grey-box + Cubist regression tree for residuals) Mixed - 10 minutes (optimization step); 1 minute (data collection) Polynomial fit and data-driven model (e.g., multivariate polynomial, regression tree) | Indoor temperature Grey-box with Fourier series + Cubist residual model 30 minutes | Energy Hard only Chilled water supply temperature, number of operating chillers |  |  |  |  | Measurement | No | 23.8667
69 | Ham et al. (2023) | 2023 | 1 | MPC | Energy and Buildings | Field site | Costa Mesa, CA, US | United States | North America | six classrooms across two buildings in a K-12 school | forced-air with six RTUs serving each classroom | 6 classrooms in two buildings | Subset of building | 504 | 30 | 3B | Cooling | High | MILP pyGLPK Not guaranteed | 2R2C gray-box RC network with lumped disturbance modeling Linear - 15 minutes (for SYSID); 5 min (LMPC); 30 min (UMPC) - | Weather (outdoor temperature, solar radiation), Electricity price Public weather forecast API (NOAA), utility tariff schedule 6–24 hours (UMPC); 15 minutes (LMPC) | Cost and peak demand minimization Mixed hard-soft RTU runtime fraction (ON/OFF), Zone temperature bounds |  |  |  |  | Measurement | No
70 | Lian et al. (2023) | 2023 | 1 | DeePC | IEEE Transactions on Control Systems Technology | Field site | Lausanne, Switzerland | Switzerland | Europe | multipurpose academic building | forced-air HP | Whole building | Whole building | 600 | 4 | 4A | Cooling | High | QP (convex reformulation of bilevel optimization) YALMIP (MATLAB) Not guaranteed (relies on convex relaxation and heuristics, no global guarantee) | Hankel matrix-based DeePC using input-output trajectories (no explicit physics-based model) Linear (LTI and LTV formulations) - 15 minutes - | Outdoor temperature, solar radiation External weather API (Tomorrow.io) - | Energy Hard only Electrical energy input (converted to setpoints for HVAC), feedback gain K |  |  |  |  | Measurement | No | 18.4
71 | Saloux et al. (2023) | 2023 | 2 | MPC | Energy | Field site | Ontario, Canada Québec, Canada | Canada | North America | central heating plants | radiant steam system with non-condensing gas boilers for heating and hot water | Whole Building | Whole building | Unknown 271,000 | 48 - 67 | 5A 6A | Heating | High | Custom brute-force search over discrete control options Custom Python-based brute-force search Global (via exhaustive search over feasible combinations) | XGBoost (for demand forecasting); data-driven boiler efficiency curves (custom nonlinear equation) Nonlinear - 60 minutes (hourly forecasting and boiler efficiency estimation) Polynomial-like fit (custom rational expression based on part-load ratio) | Heating demand (based on outdoor air temperature, time features, occupancy proxy) XGBoost 24 hours | Energy (minimize gas consumption, indirectly minimizing cost and GHG) Hard only Boiler thermal outputs, boiler selection (on/off and load assignment) |  |  |  |  | Measurement | Yes |  | 2.8 and 1.3 | 2.8 and 1.3
72 | Stoffel et al. (2024) | 2024 | 2 | MPC | Energy and Buildings | Both | Aachen, Germany | Germany | Europe | five university office spaces and a test hall in an energy facility | forced-air and radiant systems with district heating and concrete core activation | 5 office spaces Test Hall | Subset of building Whole building | 85.6 and 630 | 33 and 14 | 5A | Heating | Low | NLP IPOPT Local | Nonlinear Autoregressive with Exogenous Inputs (NARX); implemented using Multiple Linear Regression (MLR), Artificial Neural Networks (ANN), and Gaussian Process Regression (GPR) Mixed (Linear for MLR; Nonlinear for ANN and GPR) Feature lags up to 20 10 minutes (offices), 15 minutes (test hall) - | Ambient temperature, solar radiation External forecasts from DWD (Deutscher Wetterdienst) 24 hours (offices), 72 hours (test hall) | Energy (via valve position or setpoint minimization), Comfort (temperature violations), Control smoothness Mixed hard-soft Valve position (offices), AHU supply temperature setpoint, CCA flow temperature setpoint (test hall) |  |  |  |  | Measurement | No |  | 22
73 | Ham et al. (2024) | 2024 | 1 | MPC | Applied Energy | Field site | NY, US | United States | North America | subspace in a small mixed-use commercial building | forced-air with mini-split HPs and a gas furnace | Subspace in the building | Subset of building | 351.2 | 13 | 4A | Heating | High | MILP pyGLPK Not guaranteed | Grey-box 2R2C thermal network model Linear Implied multi-zone 2R2C model per zone 15 minutes Manufacturer data (rated capacities used) | Outdoor air temperature, solar radiation Weather forecast via NOAA API, solar scaling from clear-sky data 24 hours | Cost minimization, peak demand minimization, gas furnace usage reduction Mixed hard-soft Runtime fractions of heat pumps and gas furnace (RTFs), indirectly controlling zone temperature via setpoints |  |  |  |  | Measurement | No |  |  | 27
74 | Morovat et al. (2024) | 2024 | 1 | MPC | Energy | Field site | Sainte-Marthe-sur-le-Lac, Québec, Canada | Canada | North America | six classrooms in a fully electric school building | hybrid with forced-air, radiant heating, HPs, and thermal storage | six classrooms gym and office spaces | Subset of building | 378 m² (6 × 63 m²) ~200 m² | Morning Peak Load Shifting Test – 3 hours (6:00 AM – 9:00 AM) in six classrooms (378 m²). Evening Peak Load Shifting Test – 4 hours (4:00 PM – 8:00 PM) in six classrooms (378 m²). Contingency Reserve Response Test – Short-term event during peak hours in six classrooms (378 m²). Ramping Strategy Test – Multiple scenarios (1-hour, 2-hour, 3-hour ramps) in six classrooms (378 m²). Night Preheating Strategy Test – 6 hours (12:00 AM – 6:00 AM) in the gym and office spaces (~200 m²). Energy Flexibility in Radiant Floor Heating Zones Test – Full-day monitoring in the gym and office spaces (~200 m²). | 6A | Heating | High | LP CVXPy with ECOS Global | RC network Linear Third-order for convective zones, fourth-order for radiant zones 15 minutes - | Outdoor temperature, solar radiation One-day ahead weather forecast, clustering-based 1 day | Cost Hard only Zone temperature setpoints |  |  |  |  | Measurement | No |  |  | 44
75 | Lolli et al. (2024) | 2024 | 1 | MPC | Energies | Field site | Trondheim, Norway | Norway | Europe | a block of a 6-story office building | hydronic heating, mechanical ventilation, and sun-shading | Block A of the office building, which includes both open landscape offices and single offices. | Subset of building | 1520 | 40 | 6A | Heating | High |  | Encoder--decoder transformer (global transformer architecture) - - 60 minutes - | Room air temperature Transformer-based neural network 12 hours | Energy Hard only Radiator supply temperature |  |  |  |  | Measurement | No |  | 10
76 | Silvestri et al. (2024) | 2024 | 1 | RL | Applied Energy | Field site | Dübendorf, Switzerland | Switzerland | Europe | office in a modular high-performance research building | radiant hydronic TABS, hybrid VRF, and heat recovery ventilation | One office space at the lower level of the HiLo Unit | Subset of building | 22.94 | 49 | 5A | Cooling | Low |  |  |  |  | Soft actor-critic RC | Valve position continuous | Indoor temperature, weather, time, occupancy | Energy, temperature penalty Boltzmann | Simulation | No
77 | Choi et al. (2024) | 2024 | 1 | MPC | Energy | Field site | Incheon, South Korea​ | South Korea | Asia | single-zone office space in a university building | forced-air direct expansion cooling system | single-zone office space | Subset of building | 27 m² | 3 | 4A | Cooling | High | LP MATLAB linprog Not guaranteed | RC network (3R2C) Linear Two states (envelope temperature and room air temperature) 15 minutes Linear fit (COP as a linear function of outdoor temperature) | Weather (outdoor temperature, solar radiation) Weather API (forecast data), resampled 24 hours | Cost Hard only Cooling rate (translated to zone air temperature setpoint) |  |  |  |  | Measurement | No | 25.2 |  | 33.7
78 | Wang and Dong (2024) | 2024 | 3 | Data-Driven Predictive Control (DDPC), Differentiable Predictive Control (DPC) and RL | Applied Energy | Field site | Syracuse, NY, US | United States | North America | office in a small-to-medium university building | forced-air AHU with VAV and variable-speed fan | 1 office in building | Subset of building | 64.2 | DDPC: 32 (26 Succesful) DPC: 35 (25 succesful) RL: 29 (27 succesful). All over the span of eptember 19th, 2023, to February 16th, 2024. | 5A | Both | High | Nonconvex unspecified (split into two quasi-convex problems in HDDPC) - Not guaranteed | Physics-consistent input convex neural network (PCICNN) Nonlinear - 15 minutes Polynomial fit (for outdoor airflow rate via damper and fan speed curve) | Weather, Occupancy Reference to previous works used 6 hours | Multi-objective (minimize energy, maintain IEQ, ensure smooth operation) Mixed hard-soft Supply airflow rate, Outdoor airflow rate, Supply air temperature | Soft actor-critic ANN | Supply air flow and temperature set-points continuous | Indoor temperature, weather, ... | Energy, comfort, constraint penalties, smoothing Entropy-regularization | Measurement | No | HDDPC: 31.06, DPC: 17.96, RL: 38.55
79 | He et al. (2025) | 2025 | 1 | MPC | Building and Environment | Field site | Xi'an, China | China | Asia | university research laboratory | forced-air with chiller, AHU, and VAV | Office laboratory | Subset of building | 75.63 | 1 | 4B | Heating | Low | QP (with chance constraints reformulated) Sedumi Not guaranteed (feasibility and stability, but no global guarantee) | RC network (5R3C model for both temperature and relative humidity) Linear 6 state variables (Tz, Te,w, Tn,s, Wz, We,w, Wn,s) 5 minutes - | Outdoor temperature, outdoor relative humidity, solar radiation, internal gains - - | Energy, Thermal Comfort (multi-objective) Mixed hard-soft Frequencies of chilled water pump and humidifier pump |  |  |  |  | Measurement | No | 39.1
80 | Shi et al. (2025) | 2025 | 1 | DeePC | Energy and Buildings | Field site | Lausanne, Switzerland | Switzerland | Europe | multipurpose academic building | forced-air with RTU and continuous ventilation | Whole building | Whole building | 600 | 12 | 4A | Both | High | LP (day-ahead planner), QP (predictive building controller) Gurobi - | Data-driven (non-parametric) using Willems' Fundamental Lemma (Hankel matrix formulation) Linear - 15 minutes (building controller), 4 seconds (ESS controller) - | Weather (outdoor temperature, solar radiation), AGC signal Weather via Tomorrow.io API; AGC via non-parametric probabilistic method Up to 24 hours | Cost minimization, frequency regulation performance, SoC tracking Mixed hard-soft HVAC power setpoint, ESS power, intraday power transactions |  |  |  |  | Measurement | No |  |  | 28.74

## residential (tests)
# p | # t | Paper | Year | # of tests | Publication venue | Control method | Field site or laboratory? | Location | Country | Continent | Whole building or subset of building? | Floor space (m2) | Test duration (days) | Insulation level | Thermal mass | Climate zone | Heating, cooling, or both | Electricity rate structure | Control action (high level vs low level) | Benchmark | Cost savings (%) | Energy savings (%)
1 | 1 | Pedersen et al. (2013) | 2013 | 1 | 2013 10th IEEE INTERNATIONAL CONFERENCE ON NETWORKING, SENSING AND CONTROL (ICNSC) | MPC | Field site | Denmark | Denmark | Europe | Whole building |  | 152 | 0 | 2 | 5A | Heating | Dynamic | High | Measurement | 9.17
2 | 2 | Dong and Lam (2014) | 2014 | 2 | Building Simulation | MPC | Laboratory | Pittsburgh , USA | United States | North America | Whole building | 67.5 | 10 | 2 | 2 | 4A | Cooling | Flat | High | Simulation |  | 17.8
| 3 | Dong and Lam (2014) | 2014 |  |  | MPC | Laboratory | Pittsburgh , USA | United States | North America | Whole building | 67.5 | 10 | 2 | 2 | 4A | Heating | Flat | High | Simulation |  | 30.1
3 | 4 | Lindelöf et al. (2015) | 2015 | 10 | Energy and Buildings | MPC | Field site | Brugg, Switzerland | Switzerland | Europe | Whole building | 180 | 61 | 1 | 2 | 5A | Heating | Flat | High | Measurement |  | 60.4
| 5 | Lindelöf et al. (2015) | 2015 |  |  | MPC | Field site | Fey, Switzerland | Switzerland | Europe | Whole building | 240 | 113 | 0 | 0 | 5A | Heating | Flat | High | Measurement |  | 42.6
| 6 | Lindelöf et al. (2015) | 2015 |  |  | MPC | Field site | Hedingen, Switzerland | Switzerland | Europe | Whole building | 130 | 81 | 0 | 0 | 5A | Heating | Flat | High | Measurement |  | 25.5
| 7 | Lindelöf et al. (2015) | 2015 |  |  | MPC | Field site | Ihmert, Germany | Germany | Europe | Whole building | 110 | 27 | 0 | 0 | 5A | Heating | Flat | High | Measurement |  | 17.3
| 8 | Lindelöf et al. (2015) | 2015 |  |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Whole building | 280 | 64 | 0 | 0 | 5A | Heating | Flat | High | Measurement |  | 16.1
| 9 | Lindelöf et al. (2015) | 2015 |  |  | MPC | Field site | Lüdenscheid, Germany | Germany | Europe | Whole building | 65 | 94 | 0 | 0 | 5A | Heating | Flat | High | Measurement |  | 14.1
| 10 | Lindelöf et al. (2015) | 2015 |  |  | MPC | Field site | Remscheid, Germany | Germany | Europe | Whole building | 260 | 65 | 0 | 0 | 5A | Heating | Flat | High | Measurement |  | 13
| 11 | Lindelöf et al. (2015) | 2015 |  |  | MPC | Field site | Ruswil, Switzerland | Switzerland | Europe | Whole building | 200 | 138 | 0 | 0 | 5A | Heating | Flat | High | Measurement |  | 12.9
| 12 | Lindelöf et al. (2015) | 2015 |  |  | MPC | Field site | Sprockhövel, Germany | Germany | Europe | Whole building | 220 | 36 | 0 | 0 | 5A | Heating | Flat | High | Measurement |  | 10.4
| 13 | Lindelöf et al. (2015) | 2015 |  |  | MPC | Field site | Unterengstringen, Switzerland | Switzerland | Europe | Whole building | 200 | 95 | 0 | 0 | 5A | Heating | Flat | High | Measurement |  | 3.87
4 | 14 | Leurs et al. (2016) | 2016 | 1 |  | RL | Laboratory | Leuven, Belgium | Belgium | Europe | Subset of building | 61.62 | 2 | 2 | 2 | 4A | Cooling | Flat | High | Measurement
5 | 15 | Zong et al. (2017) | 2017 | 1 |  | MPC | Field site | Roskilde, Denmark | Denmark | Europe | Whole building | 150 | 10 | 1 | 2 | 5A | Heating | Dynamic | Low | Simulation | 11.3 | 5
6 | 16 | Afram and Janabi-Sharifi (2017) | 2017 | 1 | Energy and Buildings | MPC | Laboratory | Vaughan, Ontario, Canada | Canada | North America | Whole building | 342.53 | 22 | 2 | 1 | 5A | Cooling | Dynamic | High | Simulation | 79.2 | 56.55
7 | 17 | Bünning et al. (2020) | 2020 | 1 | Energy and Buildings | MPC | Field site | Dübendorf, Switzerland | Switzerland | Europe | Subset of building | 17.6 | 6 | 1 | 1 | 5A | Cooling | Flat | Low | Measurement |  | 24.9
8 | 18 | Finck et al. (2020) | 2020 | 2 | Applied Energy | MPC | Field site | near Amstelveen, Netherlands | Netherlands | Europe | Whole building | 345 | 1 | 2 | 2 | 4A | Heating | Dynamic | High | Measurement | 12
| 19 | Finck et al. (2020) | 2020 |  |  | MPC | Field site | near Amstelveen, Netherlands | Netherlands | Europe | Whole building | 345 | 1 | 2 | 2 | 4A | Heating | Dynamic | High | Measurement | 15
9 | 20 | Kurte et al. (2020) | 2020 | 1 | Sustainability | RL | Field site | Knoxville, Tennessee, USA | United States | North America | Whole building | 223 | 5 | 2 | 1 | 3A | Cooling | Dynamic | High | Simulation | 16
10 | 21 | Knudsen et al. (2021) | 2021 | 1 | Applied Energy | MPC | Laboratory | Trondheim, Norway | Norway | Europe | Whole building | 102 | 14 | 2 | 2 | 6A | Heating | Dynamic | High | Simulation | 22.5
11 | 22 | Svetozarevic et al. (2022) | 2022 | 1 |  | RL | Field site | Dübendorf, Switzerland | Switzerland | Europe | Subset of building | 17.6 | 5 | 2 | 2 | 5A | Heating | Dynamic | Low | Measurement |  | 27
12 | 23 | Bünning et al. (2022) | 2022 | 4 | Applied Energy | MPC | Field site | Dübendorf, Switzerland | Switzerland | Europe | Subset of building | 17.6 | 41 | 1 | 1 | 5A | Heating | Flat | Low | Measurement |  | 33
| 24 | Bünning et al. (2022) | 2022 |  |  | MPC | Field site | Dübendorf, Switzerland | Switzerland | Europe | Subset of building | 17.6 | 39 | 1 | 1 | 5A | Cooling | Flat | Low | Measurement |  | 32
| 25 | Bünning et al. (2022) | 2022 |  |  | MPC | Field site | Dübendorf, Switzerland | Switzerland | Europe | Subset of building | 17.6 | 41 | 1 | 1 | 5A | Heating | Flat | Low | Measurement |  | 26
| 26 | Bünning et al. (2022) | 2022 |  |  | MPC | Field site | Dübendorf, Switzerland | Switzerland | Europe | Subset of building | 17.6 | 35 | 1 | 1 | 5A | Cooling | Flat | Low | Measurement |  | 49
13 | 27 | Vivian et al. (2022) | 2022 | 1 | Applied Thermal Engineering | MPC | Laboratory | Piacenza, Italy | Italy | Europe | Whole building | 59.4 | 5 | 2 | 1 | 4A | Both | Flat | Low | Measurement | 13.5
14 | 28 | Brown and Beausoleil-Morrison (2023a) | 2023 | 1 |  | MPC | Field site | Ottawa, Canada | Canada | North America | Whole building | 149 | 13 | 2 | 1 | 6A | Both | Flat | High | Measurement |  | 40.6
15 | 29 | Wang et al. (2023) | 2023 | 2 | Energy and Buildings | MPC | Field site | Shenzhen, China | China | Asia | Subset of building | 20 | 12 | 2 | 0 | 1A | Cooling | Dynamic | High | Measurement | 22.1
| 30 | Wang et al. (2023) | 2023 |  |  | MPC | Field site | Shenzhen, China | China | Asia | Subset of building | 20 | 12 | 2 | 0 | 1A | Cooling | Dynamic | High | Measurement | 26.8
16 | 31 | Vallianos et al. (2023) | 2023 | 1 |  | MPC | Field site | Shawinigan, Québec, Canada | Canada | North America | Whole building | 180 | 3 | 2 | 2 | 6A | Heating | Dynamic | High | Measurement | 55 | 71
17 | 32 | Thorsteinsson et al. (2023) | 2023 | 4 | Applied Energy | MPC | Field site | Sjælland (Zealand), Denmark | Denmark | Europe | Whole building | 230 | 12 | 2 | 2 | 5A | Heating | Dynamic | Low | Measurement | 32.8
| 33 | Thorsteinsson et al. (2023) | 2023 |  |  | MPC | Field site | Sjælland (Zealand), Denmark | Denmark | Europe | Whole building | 230 | 10 | 2 | 2 | 5A | Heating | Dynamic | Low | Measurement | 29.1
| 34 | Thorsteinsson et al. (2023) | 2023 |  |  | MPC | Field site | Sjælland (Zealand), Denmark | Denmark | Europe | Whole building | 230 | 25 | 2 | 2 | 5A | Heating | Dynamic | Low | Measurement | 17.4
| 35 | Thorsteinsson et al. (2023) | 2023 |  |  | MPC | Field site | Sjælland (Zealand), Denmark | Denmark | Europe | Whole building | 230 | 50 | 2 | 2 | 5A | Heating | Dynamic | Low | Measurement | 2.3
18 | 36 | Brown and Beausoleil-Morrison (2023b) | 2023 | 1 | Science and Technology for the Built Environment | MPC | Field site | Ottawa, Canada | Canada | North America | Whole building | 149 | 182 | 2 | 1 | 6A | Both | Flat | High | Measurement
19 | 37 | Yin et al. (2024) | 2024 | 1 |  | MPC | Field site | Dübendorf, Switzerland | Switzerland | Europe | Subset of building | 155 | 5 | 2 | 2 | 5A | Heating | Flat | Low | Simulation
20 | 38 | Jiang et al. (2024) | 2024 | 10 | Energy and Buildings | MPC | Field site | Norman, OK | United States | North America | Whole building | 222.97 | 15 | 1 | 1 | 3A | Cooling | Dynamic | High | Measurement | 39 | 36.96
| 39 | Jiang et al. (2024) | 2024 |  |  | MPC | Field site | Miami, FL | United States | North America | Subset of building | 144 | 20 | 2 | 2 | 1A | Cooling | Dynamic | High | Measurement | 31.51 | -29.76
| 40 | Jiang et al. (2024) | 2024 |  |  | MPC | Field site | Norman, OK | United States | North America | Subset of building | 199.74 | 5 | 1 | 1 | 3A | Cooling | Dynamic | High | Measurement | -13.49 | -28.63
| 41 | Jiang et al. (2024) | 2024 |  |  | MPC | Field site | Norman, OK | United States | North America | Subset of building | 130.06 | 5 | 1 | 1 | 3A | Cooling | Dynamic | High | Measurement | 10.06 | 0
| 42 | Jiang et al. (2024) | 2024 |  |  | MPC | Field site | Norman, OK | United States | North America | Whole building | 232.26 | 6 | 1 | 1 | 3A | Cooling | Dynamic | High | Measurement | 87.06 | 91.05
| 43 | Jiang et al. (2024) | 2024 |  |  | MPC | Field site | Norman, OK | United States | North America | Whole building | 143.1 | 6 | 1 | 1 | 3A | Cooling | Dynamic | High | Measurement | 23.6 | 24.52
| 44 | Jiang et al. (2024) | 2024 |  |  | MPC | Field site | Norman, OK | United States | North America | Whole building | 167.23 | 2 | 1 | 1 | 3A | Cooling | Dynamic | High | Measurement | 46.82 | 27.4
| 45 | Jiang et al. (2024) | 2024 |  |  | MPC | Field site | Norman, OK | United States | North America | Whole building | 241.55 | 20 | 1 | 1 | 3A | Cooling | Dynamic | High | Measurement | 33.53 | 17.82
| 46 | Jiang et al. (2024) | 2024 |  |  | MPC | Field site | Norman, OK | United States | North America | Whole building | 199.74 | 10 | 1 | 1 | 3A | Cooling | Dynamic | High | Measurement | 32.05 | 26.46
| 47 | Jiang et al. (2024) | 2024 |  |  | MPC | Field site | Norman, OK | United States | North America | Whole building | 154.03 | 24 | 1 | 1 | 3A | Cooling | Dynamic | High | Measurement | 27.05 | 25.26
21 | 48 | Pergantis et al. (2024a) | 2024 | 1 | Applied Energy | MPC | Field site | West Lafayette, IN | United States | North America | Whole building | 208 | 33 | 1 | 1 | 5A | Heating | Flat | High | Measurement | 28 | 19
22 | 49 | Shamachurn et al. (2024) | 2024 | 1 |  | MPC | Field site | Reduit, Mauritius | Mauritius | Africa | Subset of building | 9 | 0.5 | 1 | 2 | 2A | Cooling | Flat | High | Measurement
23 | 50 | Pergantis et al. (2024b) | 2024 | 2 | Building and Environment | MPC | Field site | West Lafayette, IN | United States | North America | Whole building | 208 | 38 | 1 | 1 | 5A | Cooling | Flat | High | Measurement | 24.55
| 51 | Pergantis et al. (2024b) | 2024 |  |  | MPC | Field site | West Lafayette, IN | United States | North America | Whole building | 208 | 38 | 1 | 1 | 5A | Cooling | Flat | High | Measurement | 2.5
24 | 52 | Pergantis et al. (2025) | 2025 | 1 | Applied Energy | MPC | Field site | West Lafayette, IN | United States | North America | Whole building | 208 | 31 | 1 | 1 | 5A | Heating | Flat | High

## commercial (tests)
# p | # t | Paper | Year | # of tests | Journal | Control method | Field site or laboratory? | Location | Country | Continent | Whole building or subset of building? | Floor space (m2) | Test duration (days) | Insulation level | Thermal mass | Climate zone | Heating, cooling, or both | Electricity rate structure | Control action (high level vs low level) | Benchmark | Cost savings (%) | Energy savings (%)
1 | 1 | Henze et al. (2005) | 2005 | 1 | HVAC&R Research | MPC | Laboratory | Ankeny, IA, US | United States | North America | Subset of building | 198.4 | 4 | 1 | 1 | 5A | Cooling | Dynamic | High | Simulation
2 | 2 | Liu and Henze (2006b) | 2006 | 1 | Energy and Buildings | RL | Laboratory | Ankeny, IA, US | United States | North America | Subset of building | 198.4 | 6 | 1 | 1 | 5A | Cooling | Flat | High | Simulation | 8.3
3 | 3 | Kolokotsa et al. (2009) | 2009 | 1 |  | MPC | Laboratory | Chania, Crete, Greece | Greece | Europe | Subset of building | 125 | 2.7083 | 1 | 2 | 3A | Heating | Flat | Low | Simulation
4 | 4 | Liao and Dexter (2010) | 2010 | 1 | IEEE Transactions on Control Systems Technology | MPC | Field site | Garston, England | England | Europe | Whole building | 1350 | 45 | 1 | 2 | 4A | Heating | Flat | High
5 | 5 | Prívara et al. (2011) | 2011 | 2 | Energy and Buildings | MPC | Field site | Prague, Czech Republic | Czech Republic | Europe | Subset of building | 6831.425 | 45 | 2 | 2 | 5A | Heating | Flat | High | Measurement |  | 20.5
| 6 | Prívara et al. (2011) | 2011 |  |  | MPC | Field site | Prague, Czech Republic | Czech Republic | Europe | Whole building | 47830.06 | 45 | 2 | 2 | 5A | Heating | Flat | High | Measurement | 29 | 29
6 | 7 | Široký et al. (2011) | 2011 | 4 | APEN | MPC | Field site | Prague, Czech Republic | Czech Republic | Europe | Subset of building | 6831.425 | 7 | 2 | 2 | 5A | Heating | Flat | High | Measurement |  | 16.24
| 8 | Široký et al. (2011) | 2011 |  |  | MPC | Field site | Prague, Czech Republic | Czech Republic | Europe | Subset of building | 7016.68 | 49 | 2 | 2 | 5A | Heating | Flat | High | Measurement |  | 28.74
| 9 | Široký et al. (2011) | 2011 |  |  | MPC | Field site | Prague, Czech Republic | Czech Republic | Europe | Subset of building | 6646.17 | 49 | 2 | 2 | 5A | Heating | Flat | High | Measurement |  | 26.83
| 10 | Široký et al. (2011) | 2011 |  |  | MPC | Field site | Prague, Czech Republic | Czech Republic | Europe | Subset of building | 7207.21 | 49 | 1 | 2 | 5A | Heating | Flat | High | Measurement |  | 17.67
7 | 11 | Castilla et al. (2011) | 2011 | 8 | Energy and Buildings | MPC | Field site | Almeria, Spain | Spain | Europe | Subset of building | 27.38 |  | 2 | 2 | 3B | Cooling | Flat | High | Simulation
| 12 | Castilla et al. (2011) | 2011 |  |  | MPC | Field site | Almeria, Spain | Spain | Europe | Subset of building | 27.38 |  | 2 | 2 | 3B | Cooling | Flat | High | Simulation
| 13 | Castilla et al. (2011) | 2011 |  |  | MPC | Field site | Almeria, Spain | Spain | Europe | Subset of building | 27.38 |  | 2 | 2 | 3B | Cooling | Flat | High | Simulation
| 14 | Castilla et al. (2011) | 2011 |  |  | MPC | Field site | Almeria, Spain | Spain | Europe | Subset of building | 27.38 |  | 2 | 2 | 3B | Cooling | Flat | High | Simulation
| 15 | Castilla et al. (2011) | 2011 |  |  | MPC | Field site | Almeria, Spain | Spain | Europe | Subset of building | 27.38 |  | 2 | 2 | 3B | Cooling | Flat | High | Simulation
| 16 | Castilla et al. (2011) | 2011 |  |  | MPC | Field site | Almeria, Spain | Spain | Europe | Subset of building | 27.38 |  | 2 | 2 | 3B | Cooling | Flat | High | Simulation
| 17 | Castilla et al. (2011) | 2011 |  |  | MPC | Field site | Almeria, Spain | Spain | Europe | Subset of building | 27.38 |  | 2 | 2 | 3B | Cooling | Flat | High | Simulation
| 18 | Castilla et al. (2011) | 2011 |  |  | MPC | Field site | Almeria, Spain | Spain | Europe | Subset of building | 27.38 |  | 2 | 2 | 3B | Cooling | Flat | High | Simulation
8 | 19 | Aswani et al. (2012) | 2012 | 1 | Proceedings of the IEEE | MPC | Laboratory | Berkeley, CA, US | United States | North America | Subset of building | 59.46 | 3 | 1 | 1 | 3C | Cooling | Flat | High | Simulation |  | 47
9 | 20 | Ma et al. (2012a) | 2012 | 2 | IEEE Transactions on Control Systems Technology | MPC | Field site | Merced, CA, US | United States | North America | Whole building |  | 5 | 0 | 0 | 3B | Cooling | Flat | Low | Measurement
| 21 | Ma et al. (2012a) | 2012 |  |  | MPC | Field site | Merced, CA, US | United States | North America | Whole building |  | 5 | 0 | 0 | 3B | Cooling | Flat | Low | Measurement
10 | 22 | Gayeski et al. (2012) | 2012 | 2 | HVAC&R Research | MPC | Laboratory | Atlanta, GA, US | United States | North America | Whole building | 18.958 | 7 | 2 | 2 | 3A | Cooling | Flat | High | Measurement |  | 25
| 23 | Gayeski et al. (2012) | 2012 |  |  | MPC | Laboratory | Phoenix, AZ, US | United States | North America | Whole building | 18.958 | 7 | 2 | 2 | 1B | Cooling | Flat | High | Measurement |  | 19
11 | 24 | Ferreira et al. (2012) | 2012 | 2 | Energy and Buildings | MPC | Field site | Algarve, Portugal | Portugal | Europe | Subset of building |  | 2 | 0 | 0 | 3A | Cooling | Flat | High | Measurement
| 25 | Ferreira et al. (2012) | 2012 |  |  | MPC | Field site | Algarve, Portugal | Portugal | Europe | Subset of building |  | 1 | 0 | 0 | 3A | Heating | Flat | High | Measurement |  | 57
12 | 26 | Bengea et al. (2014) | 2014 | 1 | HVAC&R Research | MPC | Field site | Champaign, IL, US | United States | North America | Whole building | 650.3 | 5 | 1 | 2 | 5A | Heating | Flat | High | Measurement |  | 72.5
13 | 27 | West et al. (2014) | 2014 | 2 | Energy and Buildings | MPC | Field site | Newcastle, Australia | Australia | Oceania | Whole building | 3322 | 25 | 0 | 0 | 3A | Heating | Flat | High | Measurement | 16.9 | 14
| 28 | West et al. (2014) | 2014 |  |  | MPC | Field site | Melbourne, Australia | Australia | Oceania | Whole building | 1808 | 5 | 0 | 0 | 3A | Heating | Flat | High | Measurement |  | 32
14 | 29 | Castilla et al. (2014) | 2014 | 1 | Journal of Process Control | MPC | Field site | Almeria, Spain | Spain | Europe | Subset of building | 27.38 | 15 | 2 | 2 | 3B | Heating | Flat | High | Measurement |  | 53
15 | 30 | Váňa et al. (2014) | 2014 | 1 | Journal of Process Control | MPC | Field site | Hasselt, Belgium | Belgium | Europe | Subset of building | 3760 | 25 | 2 | 2 | 4A | Heating | Flat | High | Measurement |  | 17.07
16 | 31 | Maasoumy et al. (2014) | 2014 | 2 |  | MPC | Field site | Berkeley, CA, US | United States | North America | Whole building | 1309.9 | 0.02 | 1 | 2 | 3C | Cooling | Flat | High | Measurement
| 32 | Maasoumy et al. (2014) | 2014 |  |  | MPC | Field site | Berkeley, CA, US | United States | North America | Whole building | 1309.9 | 0.03 | 1 | 2 | 3C | Cooling | Flat | High | Measurement
17 | 33 | Preglej et al. (2014) | 2014 | 1 |  | MPC | Laboratory | Graz, Austria | Austria | Europe | Subset of building |  | 0.1 | 0 | 0 | 5A | Both | Flat | Low | Measurement |  | 44
18 | 34 | Parisio et al. (2014) | 2014 | 2 | IFAC Proceedings Volumes | MPC | Field site | Stockholm, Sweden | Sweden | Europe | Subset of building | 80 | 2 | 2 | 2 | 6A | Heating | Flat | High | Measurement
| 35 | Parisio et al. (2014) | 2014 |  |  | MPC | Field site | Stockholm, Sweden | Sweden | Europe | Subset of building | 80 | 2 | 2 | 2 | 6A | Heating | Flat | High | Measurement
19 | 36 | Parisio et al. (2015) | 2015 | 1 | 53rd IEEE Conference on Decision and Control | MPC | Laboratory | Stockholm, Sweden | Sweden | Europe | Subset of building | 80 | 1 | 2 | 2 | 6A | Cooling | Flat | High | Measurement |  | 32
20 | 37 | Goyal et al. (2015) | 2015 | 1 | APEN | MPC | Field site | Gainesville, FL, US | United States | North America | Subset of building | 21.12 | 1 | 2 | 0 | 2A | Both | Flat | High | Measurement |  | 40
21 | 38 | Zeng et al. (2015) | 2015 | 6 |  | MPC | Laboratory | Ankeny, IA, US | United States | North America | Subset of building | 99.2 | 1 | 1 | 1 | 5A | Heating | Flat | High | Simulation |  | 2.68
| 39 | Zeng et al. (2015) | 2015 |  |  | MPC | Laboratory | Ankeny, IA, US | United States | North America | Subset of building | 99.2 | 1 | 1 | 1 | 5A | Heating | Flat | High | Simulation |  | 14.29
| 40 | Zeng et al. (2015) | 2015 |  |  | MPC | Laboratory | Ankeny, IA, US | United States | North America | Subset of building | 99.2 | 1 | 1 | 1 | 5A | Heating | Flat | High | Simulation |  | 17.24
| 41 | Zeng et al. (2015) | 2015 |  |  | MPC | Laboratory | Ankeny, IA, US | United States | North America | Subset of building | 99.2 | 1 | 1 | 1 | 5A | Heating | Flat | High | Simulation |  | 2.23
| 42 | Zeng et al. (2015) | 2015 |  |  | MPC | Laboratory | Ankeny, IA, US | United States | North America | Subset of building | 99.2 | 1 | 1 | 1 | 5A | Heating | Flat | High | Simulation |  | 10.3
| 43 | Zeng et al. (2015) | 2015 |  |  | MPC | Laboratory | Ankeny, IA, US | United States | North America | Subset of building | 99.2 | 1 | 1 | 1 | 5A | Heating | Flat | High | Simulation |  | 16.94
22 | 44 | Huang et al. (2015) | 2015 | 1 | Building and Environment | MPC | Field site | Adelaide, Australia | Australia | Oceania | Subset of building |  | 1 | 1 | 2 | 3B | Cooling | Dynamic | Low | Measurement | 13
23 | 45 | Li et al. (2015) | 2015 | 1 | Science and Technology for the Built Environment | MPC | Field site | Philadelphia, PA, US | United States | North America | Subset of building |  | 20 | 1 | 2 | 4A | Cooling | Flat | High | Measurement |  | 33
24 | 46 | Kim et al. (2015) | 2015 | 1 | Energy and Buildings | MPC | Field site | Knoxville, TN, US | United States | North America | Subset of building | 929 | 4 | 1 | 2 | 3A | Cooling | Flat | High | Measurement |  | 8
25 | 47 | Sturzenegger et al. (2016) | 2016 | 4 | IEEE Transactions on Control Systems Technology | MPC | Field site | Allschwil, Switzerland | Switzerland | Europe | Whole building | 6000 | 98 | 2 | 2 | 4A | Cooling | Flat | High | Simulation
| 48 | Sturzenegger et al. (2016) | 2016 |  |  | MPC | Field site | Allschwil, Switzerland | Switzerland | Europe | Whole building | 6000 | 31 | 2 | 2 | 4A | Heating | Flat | High | Simulation
| 49 | Sturzenegger et al. (2016) | 2016 |  |  | MPC | Field site | Allschwil, Switzerland | Switzerland | Europe | Whole building | 6000 | 55 | 2 | 2 | 4A | Heating | Dynamic | High | Simulation
| 50 | Sturzenegger et al. (2016) | 2016 |  |  | MPC | Field site | Allschwil, Switzerland | Switzerland | Europe | Whole building | 6000 | 10 | 2 | 2 | 4A | Heating | Dynamic | High | Simulation
26 | 51 | De Coninck and Helsen (2016) | 2016 | 1 | Energy and Buildings | MPC | Field site | Brussels, Belgium | Belgium | Europe | Whole building | 960 | 15 | 2 | 2 | 4A | Heating | Dynamic | High | Measurement | 37 | 25
27 | 52 | Ruano et al. (2016) | 2016 | 1 |  | MPC | Field site | Faro, Portugal | Faro | Europe | Subset of building | 131.25 | 0.25 | 0 | 0 | 3A | Cooling | Dynamic | High | Measurement |  | 50
28 | 53 | Costanzo et al. (2016) | 2016 | 1 |  | RL | Laboratory | Genk, Belgium | Belgium | Europe | Subset of building | 61.62 | 16 | 0 | 0 | 4A | Cooling | Dynamic | High
29 | 54 | Fabietti et al. (2016) | 2016 | 4 |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 90 | 0.5 | 2 | 2 | 4A | Heating | Flat | High | Simulation
| 55 | Fabietti et al. (2016) | 2016 |  |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 90 | 0.5 | 2 | 2 | 4A | Heating | Flat | High | Simulation
| 56 | Fabietti et al. (2016) | 2016 |  |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 90 | 0.5 | 2 | 2 | 4A | Heating | Flat | High | Simulation
| 57 | Fabietti et al. (2016) | 2016 |  |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 90 | 0.5 | 2 | 2 | 4A | Heating | Flat | High | Simulation
30 | 58 | Vrettos et al. (2016) | 2016 | 6 |  | MPC | Laboratory | Berkeley, CA, US | United States | North America | Subset of building | 60 | 1 | 0 | 0 | 3C | Cooling | Flat | Low | Measurement
| 59 | Vrettos et al. (2016) | 2016 |  |  | MPC | Laboratory | Berkeley, CA, US | United States | North America | Subset of building | 60 | 1 | 0 | 0 | 3C | Cooling | Flat | Low | Measurement
| 60 | Vrettos et al. (2016) | 2016 |  |  | MPC | Laboratory | Berkeley, CA, US | United States | North America | Subset of building | 60 | 1 | 0 | 0 | 3C | Cooling | Flat | Low | Measurement
| 61 | Vrettos et al. (2016) | 2016 |  |  | MPC | Laboratory | Berkeley, CA, US | United States | North America | Subset of building | 60 | 1 | 0 | 0 | 3C | Cooling | Flat | Low | Measurement
| 62 | Vrettos et al. (2016) | 2016 |  |  | MPC | Laboratory | Berkeley, CA, US | United States | North America | Subset of building | 60 | 1 | 0 | 0 | 3C | Cooling | Flat | Low | Measurement
| 63 | Vrettos et al. (2016) | 2016 |  |  | MPC | Laboratory | Berkeley, CA, US | United States | North America | Subset of building | 60 | 1 | 0 | 0 | 3C | Cooling | Flat | Low | Measurement
31 | 64 | Gorecki et al. (2017) | 2017 | 10 |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 115 | 1 | 1 | 2 | 4A | Heating | Dynamic | Low | Simulation
| 65 | Gorecki et al. (2017) | 2017 |  |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 115 | 1 | 1 | 2 | 4A | Heating | Dynamic | Low | Simulation
| 66 | Gorecki et al. (2017) | 2017 |  |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 115 | 1 | 1 | 2 | 4A | Heating | Dynamic | Low | Simulation
| 67 | Gorecki et al. (2017) | 2017 |  |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 115 | 1 | 1 | 2 | 4A | Heating | Dynamic | Low | Simulation
| 68 | Gorecki et al. (2017) | 2017 |  |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 115 | 1 | 1 | 2 | 4A | Heating | Dynamic | Low | Simulation
| 69 | Gorecki et al. (2017) | 2017 |  |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 115 | 1 | 1 | 2 | 4A | Heating | Dynamic | Low | Simulation
| 70 | Gorecki et al. (2017) | 2017 |  |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 115 | 1 | 1 | 2 | 4A | Heating | Dynamic | Low | Simulation
| 71 | Gorecki et al. (2017) | 2017 |  |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 115 | 1 | 1 | 2 | 4A | Heating | Dynamic | Low | Simulation
| 72 | Gorecki et al. (2017) | 2017 |  |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 115 | 1 | 1 | 2 | 4A | Heating | Dynamic | Low | Simulation
| 73 | Gorecki et al. (2017) | 2017 |  |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Subset of building | 115 | 1 | 1 | 2 | 4A | Heating | Dynamic | Low | Simulation
32 | 74 | Schmidt et al. (2017) | 2017 | 3 |  | MPC | Field site | Granada, Spain | Spain | Europe | Whole building |  | 43 | 1 | 2 | 3A | Heating | Flat | High | Measurement |  | 33
| 75 | Schmidt et al. (2017) | 2017 |  |  | MPC | Field site | Granada, Spain | Spain | Europe | Whole building |  | 43 | 1 | 2 | 3A | Heating | Flat | High | Measurement
| 76 | Schmidt et al. (2017) | 2017 |  |  | RL | Field site | Granada, Spain | Spain | Europe | Whole building |  | 43 | 1 | 2 | 3A | Heating | Flat | High | Measurement
33 | 77 | Stauffer et al. (2017) | 2017 | 2 | Energy Procedia | MPC | Field site | Neuchâtel, Switzerland | Switzerland | Europe | Subset of building | 120 | 38 | 1 | 1 | 4A | Cooling | Flat | High | Measurement | 22
| 78 | Stauffer et al. (2017) | 2017 |  |  | MPC | Field site | Winterthur, Switzerland | Switzerland | Europe | Whole building | 2100 | 10 | 1 | 1 | 5A | Heating | Flat | High | Measurement
34 | 79 | Hilliard et al. (2017) | 2017 | 1 | Building and Environment | MPC | Field site | Halifax, Canada | Canada | North America | Whole building | 10000 | 113 | 2 | 1 | 5A | Heating | Flat | High | Measurement |  | 29
35 | 80 | Killian and Kozek (2018) | 2018 | 1 |  | MPC | Field site | Salzburg, Austria | Austria | Europe | Subset of building | 13000 | 49 | 2 | 2 | 5A | Heating | Flat | High | Simulation
36 | 81 | Zhuang et al. (2018) | 2018 | 1 | Building and Environment | MPC | Field site | Sichuan Province, China | China | Asia | Whole building | 30750 | 1 | 2 | 2 | 3A | Cooling | Flat | High | Measurement |  | 16
37 | 82 | Michailidis et al. (2018) | 2018 | 1 |  | RL | Field site | Aachen, Germany | Germany | Europe | Subset of building | 93 | 5 | 2 | 2 | 5A | Heating | Flat | High | Measurement |  | 34.7
38 | 83 | Lindelöf et al. (2018) | 2018 | 1 | Energy Procedia | MPC | Field site | Sargans, Switzerland | Switzerland | Europe | Whole building | 2700 | 58 | 1 | 2 | 4A | Heating | Flat | High | Measurement |  | 31.9
39 | 84 | Viot et al. (2018) | 2018 | 1 | Energy and Buildings | MPC | Field site | Bordeaux, France | France | Europe | Subset of building | 200 | 30 | 0 | 0 | 3A | Heating | Flat | High | Simulation |  | 35
40 | 85 | Granderson et al. (2018) | 2018 | 4 | Energy and Buildings | MPC | Field site | Long Beach, CA, US | United States | North America | Whole building | 15608 | 170 | 1 | 1 | 3C | Cooling | Flat | High | Measurement |  | 1.4
| 86 | Granderson et al. (2018) | 2018 |  |  | MPC | Field site | Dayton, OH, US | United States | North America | Whole building | 15621 | 108 | 1 | 2 | 4A | Cooling | Flat | High | Measurement |  | 8.9
| 87 | Granderson et al. (2018) | 2018 |  |  | MPC | Field site | New York, NY, US | United States | North America | Whole building | 27871 | 113 | 2 | 2 | 4C | Cooling | Flat | High | Measurement |  | -0.4
| 88 | Granderson et al. (2018) | 2018 |  |  | MPC | Field site | Washington, D.C., US | United States | North America | Whole building | 21832 | 148 | 1 | 2 | 4A | Cooling | Flat | High | Measurement |  | 1.9
41 | 89 | Joe et al. (2018) | 2018 | 1 | Energy and Buildings | MPC | Field site | West Lafayette, IN, US | United States | North America | Subset of building | 103.95 | 11 | 2 | 2 | 5A | Cooling | Flat | High | Simulation |  | 27
42 | 90 | Kim and Braun (2018) | 2018 | 2 | Energy and Buildings | MPC | Laboratory | West Lafayette, IN, US | United States | North America | Subset of building | 105 | 3 | 1 | 1 | 5A | Cooling | Flat | High | Measurement |  | 14
| 91 | Kim and Braun (2018) | 2018 |  | Energy and Buildings | MPC | Field site | FL, US | United States | North America | Whole building | 1400 | 60 | 1 | 1 | 4C | Cooling | Flat | High | Measurement |  | 12.95
43 | 92 | Joe and Karava (2019) | 2019 | 5 | APEN | MPC | Field site | West Lafayette, IN, US | United States | North America | Subset of building | 103.95 | 10 | 2 | 2 | 5A | Cooling | Dynamic | Low | Simulation | 34.72 | 15.79
| 93 | Joe and Karava (2019) | 2019 |  |  | MPC | Field site | West Lafayette, IN, US | United States | North America | Subset of building | 103.95 | 10 | 2 | 2 | 5A | Cooling | Dynamic | Low | Simulation | 50.53 | 35.35
| 94 | Joe and Karava (2019) | 2019 |  |  | MPC | Field site | West Lafayette, IN, US | United States | North America | Subset of building | 103.95 | 10 | 2 | 2 | 5A | Cooling | Dynamic | Low | Measurement | 75 | 58
| 95 | Joe and Karava (2019) | 2019 |  |  | MPC | Field site | West Lafayette, IN, US | United States | North America | Subset of building | 103.95 | 10 | 2 | 2 | 5A | Heating | Flat | Low | Simulation |  | 16
| 96 | Joe and Karava (2019) | 2019 |  |  | MPC | Field site | West Lafayette, IN, US | United States | North America | Subset of building | 103.95 | 10 | 2 | 2 | 5A | Heating | Flat | Low | Measurement |  | 29
44 | 97 | Lee et al. (2019) | 2019 | 1 | Energy and Buildings | MPC | Field site | West Lafayette, IN, US | United States | North America | Subset of building | 103.95 | 19 | 2 | 2 | 5A | Cooling | Flat | High | Measurement
45 | 98 | Zhang et al. (2019) | 2019 | 1 |  | RL | Field site | Pittsburgh, PA, US | United States | North America | Whole building | 600 | 78 | 1 | 1 | 4A | Heating | Flat | High | Measurement |  | 16.7
46 | 99 | Yang et al. (2019) | 2019 | 2 | Energy and Buildings | MPC | Laboratory | Singapore | Singapore | Asia | Subset of building | 43.5 | 1 | 2 | 1 | 0A | Cooling | Flat | High | Measurement |  | 14.7
| 100 | Yang et al. (2019) | 2019 |  |  | MPC | Laboratory | Singapore | Singapore | Asia | Subset of building | 43.5 | 1 | 2 | 1 | 0A | Cooling | Flat | High | Measurement |  | 20
47 | 101 | Yang et al. (2020a) | 2020 | 2 | APEN | MPC | Field site | Singapore | Singapore | Asia | Subset of building | 255 | 14 | 2 | 2 | 0A | Cooling | Flat | High | Measurement |  | 16
| 102 | Yang et al. (2020a) | 2020 |  |  | MPC | Field site | Singapore | Singapore | Asia | Subset of building | 255 | 14 | 2 | 2 | 0A | Cooling | Flat | High | Measurement |  | 18
48 | 103 | Cotrufo et al. (2020) | 2020 | 1 |  | MPC | Field site | Varennes, Québec, Canada | Canada | North America | Whole building |  | 70 | 0 | 0 | 6A | Heating | Flat | High | Measurement |  | 22.2
49 | 104 | Drgoňa et al. (2020) | 2020 | 1 | Journal of Process Control | MPC | Field site | Hasselt, Belgium | Belgium | Europe | Subset of building | 3760 | 35 | 2 | 2 | 4A | Both | Flat | High | Measurement |  | 53.5
50 | 105 | Yang et al. (2020b) | 2020 | 2 | APEN | MPC | Field site | Singapore | Singapore | Asia | Subset of building | 46 | 10 | 1 | 2 | 0A | Cooling | Flat | High | Measurement |  | 36.7
| 106 | Yang et al. (2020b) | 2020 |  |  | MPC | Field site | Singapore | Singapore | Asia | Subset of building | 255 | 10 | 1 | 2 | 0A | Cooling | Flat | High | Measurement |  | 58.5
51 | 107 | Chen et al. (2020) | 2020 | 1 | Frontiers in Built Environment | RL | Field site | Pittsburgh, PA, US | United States | North America | Subset of building | 20 | 21 | 0 | 0 | 4A | Cooling | Flat | Low | Measurement |  | 16.7
52 | 108 | Freund and Schmitz (2021) | 2021 | 1 | Building and Environment | MPC | Field site | Hamburg, Germany | Germany | Europe | Whole building | 2270 | 90 | 2 | 2 | 5A | Heating | Flat | High | Measurement |  | 30
53 | 109 | Sampaio et al. (2021) | 2021 | 2 |  | MPC | Field site | Brussels, Belgium | Belgium | Europe | Whole building | 25000 | 10 | 2 | 2 | 4A | Cooling | Flat | High | Simulation |  | 8.6
| 110 | Sampaio et al. (2021) | 2021 |  |  | MPC | Field site | Brussels, Belgium | Belgium | Europe | Whole building | 25000 | 17 | 1 | 1 | 4A | Heating | Flat | High | Simulation |  | 11.7
54 | 111 | Yang et al. (2021) | 2021 | 3 |  | MPC | Laboratory | Singapore | Singapore | Asia | Subset of building | 43.5 | 2 | 2 | 1 | 0A | Cooling | Flat | Low | Measurement |  | 18.4
| 112 | Yang et al. (2021) | 2021 |  |  | MPC | Laboratory | Singapore | Singapore | Asia | Subset of building | 43.5 | 2 | 2 | 1 | 0A | Cooling | Flat | Low | Measurement |  | 22.2
| 113 | Yang et al. (2021) | 2021 |  |  | MPC | Laboratory | Singapore | Singapore | Asia | Subset of building | 43.5 | 1 | 2 | 1 | 0A | Cooling | Flat | Low | Measurement |  | 23.8
55 | 114 | Touzani et al. (2021) | 2021 | 3 | APEN | RL | Laboratory | Berkeley, CA, US | United States | North America | Subset of building | 57 | 7 | 2 | 0 | 3C | Cooling | Flat | High | Measurement | 0.6
| 115 | Touzani et al. (2021) | 2021 |  |  | RL | Laboratory | Berkeley, CA, US | United States | North America | Subset of building | 57 | 7 | 2 | 0 | 3C | Cooling | Dynamic | High | Measurement | 39.6
| 116 | Touzani et al. (2021) | 2021 |  |  | RL | Laboratory | Berkeley, CA, US | United States | North America | Subset of building | 57 | 7 | 2 | 0 | 3C | Cooling | Dynamic | High | Measurement | 29.4
56 | 117 | Jung et al. (2022) | 2022 | 5 |  | RL | Laboratory | Seoul, South Korea | South Korea | Asia | Subset of building | 10.92 | 0.02 | 0 | 0 | 4A | Both | Flat | High | Measurement
| 118 | Jung et al. (2022) | 2022 |  |  | RL | Laboratory | Seoul, South Korea | South Korea | Asia | Subset of building | 10.92 | 0.02 | 0 | 0 | 4A | Both | Flat | High | Measurement
| 119 | Jung et al. (2022) | 2022 |  |  | RL | Laboratory | Seoul, South Korea | South Korea | Asia | Subset of building | 10.92 | 0.02 | 0 | 0 | 4A | Both | Flat | High | Measurement
| 120 | Jung et al. (2022) | 2022 |  |  | RL | Laboratory | Seoul, South Korea | South Korea | Asia | Subset of building | 10.92 | 0.02 | 0 | 0 | 4A | Both | Flat | High | Measurement
| 121 | Jung et al. (2022) | 2022 |  |  | RL | Laboratory | Seoul, South Korea | South Korea | Asia | Subset of building | 10.92 | 0.02 | 0 | 0 | 4A | Both | Flat | High | Measurement
57 | 122 | Arroyo et al. (2022) | 2022 | 3 |  | MPC | Laboratory | Heverlee, Belgium | Belgium | Europe | Subset of building | 6.21 | 69 | 2 | 2 | 4A | Heating | Dynamic | Low | Measurement
| 123 | Arroyo et al. (2022) | 2022 |  |  | MPC | Laboratory | Heverlee, Belgium | Belgium | Europe | Subset of building | 6.21 | 60 | 2 | 2 | 4A | Heating | Dynamic | Low | Measurement
| 124 | Arroyo et al. (2022) | 2022 |  |  | MPC | Laboratory | Heverlee, Belgium | Belgium | Europe | Subset of building | 6.21 | 57 | 2 | 2 | 4A | Heating | Dynamic | Low | Measurement
58 | 125 | Kim and Braun (2022) | 2022 | 2 | Building and Environment | MPC | Field site | West Lafayette, IN, US | United States | North America | Subset of building | 105 | 5 | 1 | 1 | 5A | Cooling | Dynamic | High | Measurement | 3.61
| 126 | Kim and Braun (2022) | 2022 |  |  | MPC | Field site | West Lafayette, IN, US | United States | North America | Subset of building | 105 | 15 | 1 | 1 | 5A | Cooling | Dynamic | High | Measurement | 8.67
59 | 127 | Blum et al. (2022) | 2022 | 1 | APEN | MPC | Field site | Berkeley, CA, US | United States | North America | Subset of building | 6038 | 31 | 2 | 2 | 3C | Both | Flat | Low | Measurement |  | 40
60 | 128 | Naug et al. (2022) | 2022 | 1 | Proceedings of the Annual Conference of the Prognostics and Health Management Society, PHM | RL | Field site | Nashville, TN, US | United States | North America | Whole building | 2958.776 | 365 | 2 | 2 | 4A | Both | Flat | High | Measurement |  | 13.6
61 | 129 | Kim et al. (2022) | 2022 | 1 | APEN | MPC | Field site | Merced, CA, US | United States | North America | Whole building |  | 7 | 2 | 2 | 3B | Cooling | Dynamic | Low | Measurement
62 | 130 | Zhang et al. (2022) | 2022 | 1 | Advances in APEN | MPC | Field site | Blue Lake Rancheria, CA, US | United States | North America | Whole building | 418 | 365 | 1 | 1 | 4C | Both | Dynamic | High | Measurement | 11.7
63 | 131 | Maddalena et al. (2022) | 2022 | 1 |  | MPC | Field site | Campo Grande, Brazil | Brazil | South America | Subset of building |  | 4 | 1 | 2 | 1A | Cooling | Flat | Low | Simulation
64 | 132 | Lei et al. (2022) | 2022 | 1 |  | RL | Field site | Singapore | Singapore | Asia | Subset of building | 164 | 10 | 2 | 2 | 0A | Cooling | Flat | Low | Measurement |  | 14
65 | 133 | Luo et al. (2022) | 2022 | 2 | DeepMind | RL | Field site | US | United States | North America | Whole building |  | 90 | 0 | 0 |  | Cooling | Flat | Low | Measurement |  | 9
| 134 | Luo et al. (2022) | 2022 |  |  | RL | Field site | US | United States | North America | Whole building |  | 90 | 0 | 0 |  | Cooling | Flat | Low | Measurement |  | 13
66 | 135 | Zhan et al. (2023) | 2023 | 1 | Energy and Buildings | MPC | Field site | Singapore | Singapore | Asia | Subset of building | 320 | 49 | 0 | 0 | 0A | Cooling | Flat | High | Simulation
67 | 136 | Zhang et al. (2023) | 2023 | 2 | Energy and Buildings | MPC | Field site | West Lafayette, IN, US | United States | North America | Subset of building | 12.21 | 1 | 2 | 2 | 5A | Both | Flat | High | Measurement |  | 28
| 137 | Zhang et al. (2023) | 2023 |  |  | MPC | Field site | West Lafayette, IN, US | United States | North America | Subset of building | 12.21 | 1 | 2 | 2 | 5A | Both | Flat | High | Measurement |  | 35
68 | 138 | Yue et al. (2023) | 2023 | 1 |  | MPC | Field site | Zhejiang province, China | China | Asia | Whole building | 16500 | 15 | 0 | 0 | 3A | Cooling | Flat | High | Measurement |  | 23.8667
69 | 139 | Ham et al. (2023) | 2023 | 1 | Energy and Buildings | MPC | Field site | Costa Mesa, CA, US | United States | North America | Subset of building | 504 | 30 | 2 | 2 | 3B | Cooling | Dynamic | High | Measurement
70 | 140 | Lian et al. (2023) | 2023 | 1 |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Whole building | 600 | 4 | 1 | 1 | 4A | Cooling | Flat | Low | Measurement |  | 18.4
71 | 141 | Saloux et al. (2023) | 2023 | 2 |  | MPC | Field site | Ontario, Canada | Canada | North America | Whole building |  | 48 | 0 | 0 | 5A | Heating | Flat | High | Measurement | 2.8 | 2.8
| 142 | Saloux et al. (2023) | 2023 |  |  | MPC | Field site | Québec, Canada | Canada | North America | Whole building | 271000 | 67 | 0 | 0 | 6A | Heating | Flat | High | Measurement | 1.3 | 1.3
72 | 143 | Stoffel et al. (2024) | 2024 | 2 | Energy and Buildings | MPC | Field site | Aachen, Germany | Germany | Europe | Subset of building | 85.6 | 33 | 1 | 1 | 5A | Heating | Flat | Low | Measurement |  | 22
| 144 | Stoffel et al. (2024) | 2024 |  |  | MPC | Laboratory | Aachen, Germany | Germany | Europe | Whole building | 630 | 14 | 2 | 2 | 5A | Heating | Flat | Low | Measurement
73 | 145 | Ham et al. (2024) | 2024 | 1 | APEN | MPC | Field site | NY, US | United States | North America | Subset of building | 351.2 | 13 | 2 | 2 | 4A | Heating | Dynamic | High | Measurement | 27
74 | 146 | Morovat et al. (2024) | 2024 | 1 |  | MPC | Field site | Sainte-Marthe-sur-le-Lac, Québec, Canada | Canada | North America | Subset of building | 378 | 1 | 2 | 2 | 6A | Heating | Dynamic | High | Measurement | 44
75 | 147 | Lolli et al. (2024) | 2024 | 1 |  | MPC | Field site | Trondheim, Norway | Norway | Europe | Subset of building | 1520 | 40 | 1 | 1 | 6A | Heating | Flat | High | Measurement |  | 10
76 | 148 | Silvestri et al. (2024) | 2024 | 1 | APEN | RL | Field site | Dübendorf, Switzerland | Switzerland | Europe | Subset of building | 22.94 | 49 | 2 | 2 | 5A | Cooling | Flat | Low | Simulation
77 | 149 | Choi et al. (2024) | 2024 | 1 |  | MPC | Field site | Incheon, South Korea​ | South Korea | Asia | Subset of building | 27 | 3 | 1 | 1 | 4A | Cooling | Dynamic | High | Measurement | 33.7 | 25.2
78 | 150 | Wang and Dong (2024) | 2024 | 3 | APEN | MPC | Field site | Syracuse, NY, US | United States | North America | Subset of building | 64.2 | 26 | 1 | 1 | 5A | Both | Flat | High | Measurement |  | 31.06
| 151 | Wang and Dong (2024) | 2024 |  |  | MPC | Field site | Syracuse, NY, US | United States | North America | Subset of building | 64.2 | 25 | 1 | 1 | 5A | Both | Flat | High | Measurement |  | 17.96
| 152 | Wang and Dong (2024) | 2024 |  |  | RL | Field site | Syracuse, NY, US | United States | North America | Subset of building | 64.2 | 27 | 1 | 1 | 5A | Both | Flat | High | Measurement |  | 38.55
79 | 153 | He et al. (2025) | 2025 | 1 |  | MPC | Field site | Xi'an, China | China | Asia | Subset of building | 75.63 | 1 | 2 | 2 | 4B | Heating | Flat | Low | Measurement |  | 39.1
80 | 154 | Shi et al. (2025) | 2025 | 1 |  | MPC | Field site | Lausanne, Switzerland | Switzerland | Europe | Whole building | 600 | 12 | 1 | 1 | 4A | Both | Flat | Low | Measurement | 28.74